## Example
No.I Mode: 18 Core From "PSL"Phongsaly to "PSL"BounNuea
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 1.373 | 0.35 | 0.25 | 16 | Fail | 1.373
2 | Free | 1.373 | 0.35 | 0.25 | 16 | Fail | 1.373
3 | PDH |  |  |  | 16 | Pass | No | PSL- Bounneua
4 | PDH |  |  |  | 16 | Pass | No | PSL- Bounneua
5 | PDH |  |  |  | 16 | Pass | No | PSL- Phiengdorkkham
6 | Free | 40.342 | 11.792 | 0.28 | 16 | Pass | No
7 | Free | 40.342 | 12.02 | 0.31 | 16 | Pass | No
8 | STM-16 |  |  |  | 16 | Pass | No | PSL- Bounneua
9 | STM-16 |  |  |  | 16 | Pass | No | PSL- Bounneua
10 | PDH |  |  |  | 16 | Pass | No | PSL- Phiengdorkkham
11 | Free | 39.007 | 8.594 | 0.28 | 16 | Fail | 39.007
12 | Free | 40.336 | 11.792 | 0.28 | 16 | Pass | No
13 | PDH |  |  |  | 16 | Pass | No | PSL- Km 33
14 | PDH |  |  |  | 16 | Pass | No | PSL- Km 33
15 | Free | 33.434 | 8.89 | 0.28 | 16 | Fail | 33.434
16 | Free | 33.434 | 8.89 | 0.28 | 16 | Fail | 33.434
17 | Free | 32.556 | 8.89 | 0.28 | 16 | Fail | 32.556
18 | Free | 32.556 | 8.9 | 0.28 | 16 | Fail | 32.556
No.II Mode: 18 Core From "PSL"Bounneua to "PSL"Ban Yor
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 3.158 | 0.779 | 0.246 | 8 | Fail | 3.158
2 | Free | 4.073 | 0.983 | 0.241 | 8 | Fail | 4.073
3 | HP |  |  |  | 8 | Pass | No | PSL- Phiengdorkkham
4 | HP |  |  |  | 8 | Pass | No | PSL- Phiengdorkkham
5 | LTC |  |  |  | 8 | Pass | No | Bounneua ETL - Danpakha LTC
6 | Free | 3.158 | 0.779 | 0.246 | 8 | Fail | 3.158
7 | Free | 1.252 | 0.31 | 0.25 | 8 | Fail | 1.252
8 | PDH |  |  |  | 8 | Pass | No | Bounneua - Danpakha
9 | PDH |  |  |  | 8 | Pass | No | Bounneua - Danpakha
10 | Free | 6.577 | 1.438 | 0.26 | 8 | Fail | 6.577
11 | Free | 22.577 | 5.326 | 0.235 | 8 | Pass | No
12 | Free | 22.577 | 7.906 | 0.31 | 8 | Pass | No
13 | HP |  |  |  | 8 | Pass | No | HP 230 kv
14 | STM-16 |  |  |  | 8 | Pass | No | Bounneu - Bountai
15 | STM-16 |  |  |  | 8 | Pass | No | Bounneu - Bountai
16 | Free | 22.577 | 5.326 | 0.31 | 8 | Pass | No
17 | LTC |  |  |  | 8 | Pass | No | Bounneua ETL - Danpakha LTC
18 | Free | 22.577 | 5.326 | 0.31 | 8 | Pass | No
No.III Mode: 18 Core From "PSL"Ban Yor to "PSL"Bountai
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 17.745 | 4.764 | 0.268 | 14 | Fail | 17.745
2 | Free | 17.745 | 4.764 | 0.268 | 14 | Fail | 17.745
3 | Free | 17.745 | 4.764 | 0.268 | 14 | Fail | 17.745
4 | Free | 10.692 | 4.764 | 0.35 | 14 | Fail | 10.692
5 | PDH |  |  |  | 14 | Pass | No | Ban Yor - Bountai
6 | STM-16 |  |  |  | 14 | Pass | No | Bounneu - Bountai
7 | Free | 33.216 | 7.935 | 0.238 | 14 | Pass | No
8 | PDH |  |  |  | 14 | Pass | No | Ban Yor - Bountai
9 | STM-16 |  |  |  | 14 | Pass | No | Bounneu - Bountai
10 | Free | 1.249 | 0.266 | 0.212 | 14 | Fail | 1.249
11 | HP |  |  |  | 14 | Fail |  | HP 230 kv
12 | Free | 33.221 | 7.473 |  | 14 | Fail | 33.221
13 | Free | 10.337 | 2.026 | 0.195 | 14 | Fail | 10.337
14 | Free | 10.337 | 2.221 | 0.195 | 14 | Fail | 10.337
15 | Free | 3.574 | 0.796 | 0.221 | 14 | Fail | 3.574
16 | Free | 5.801 | 1.333 | 0.229 | 14 | Fail | 5.801
17 | Free | 3.574 | 0.829 | 0.801 | 14 | Fail | 3.574
18 | Free | 3.579 | 0.829 | 0.801 | 14 | Fail | 3.579
No.IV Mode: 18 Core From "PSL"Bountai to "PSL"Peture
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | RPT |  |  |  | 18 | Pass | No | RPT - Phialek
2 | Free | 14.2 | 3.89 | 0.28 | 18 | Fail | 14.2
3 | Free | 7.222 | 1.98 | 0.24 | 18 | Fail | 7.222
4 | Free | 7.222 | 1.98 | 0.24 | 18 | Fail | 7.222
5 | PDH |  |  |  | 18 | Pass |  | Bountai - Namly
6 | Free | 14.2 | 4.02 | 0.25 | 18 | Fail | 14.2
7 | STM-16 |  |  |  | 18 | Pass | No | Bountai - Parknamnoy
8 | STM-16 |  |  |  | 18 | Pass | No | Bountai - Parknamnoy
9 | Free | 49.38 | 14.02 | 0.28 | 18 | Pass | No
10 | PDH |  |  |  | 18 | Pass | No | Bountai - Namly
11 | Free | 44.948 | 13.918 | 0.29 | 18 | Fail | 44.948
12 | Free | 42 | 12.02 | 0.29 | 18 | Fail | 42
13 | STM-4 |  |  |  | 18 | Pass | No | Bountai - Parknamnoy
14 | STM-4 |  |  |  | 18 | Pass | No | Bountai -Sumphunxay
15 | STM-4 |  |  |  | 18 | Pass | No | Bountai - Parknamnoy
16 | STM-4 |  |  |  | 18 | Pass | No | Bountai -Sumphunxay
17 | Free | 49.38 | 14.05 | 0.29 | 18 | Pass | No
18 | Free | 49.38 | 14.02 | 0.29 | 18 | Pass | No
No.V Mode: 18 Core From "PSL"Peture to "PSL"Paknamnoy
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 |  | 1.512 | 0.441 | 0.291 | 13 | Fail | 1.512
2 |  | 27.343 | 9.155 | 0.334 | 13 | Pass | No
3 | STM-16 |  |  |  | 13 | Pass | No | Bountai - Parknamnoy
4 | STM-16 |  |  |  | 13 | Pass | No | Bountai - Parknamnoy
5 |  | 27.343 | 7.385 | 0.269 | 13 | Pass | No
6 |  | 27.343 | 7.385 | 0.269 | 13 | Pass | No
7 |  | 27.343 | 7.385 | 0.269 | 13 | Pass | No
8 |  | 12.831 | 2.755 | 0.214 | 13 | Fail | 12.831
9 |  | 12.831 | 2.755 | 0.214 | 13 | Fail | 12.831
10 | STM-4 |  |  |  | 13 | Pass | No | Bountai - Parknamnoy
11 |  | 27.343 | 7.385 | 0.269 | 13 | Fail
12 | STM-4 |  |  |  | 13 | Pass |  | Bountai - Parknamnoy
13 | PDH |  |  |  | 13 | Pass |  | Peture - Parknamnoy
14 | PDH |  |  |  | 13 | Pass |  | Peture - Parknamnoy
15 |  | 1.343 | 0.427 | 0.317 | 13 | Fail | 1.343
16 |  | 1.344 | 0.472 | 0.317 | 13 | Fail | 1.344
17 |  | 1.345 | 0.517 | 0.317 | 13 | Fail | 1.345
18 |  | 1.346 | 0.562 | 0.317 | 13 | Fail | 1.346
No.VI Mode: 18 Core From "PSL"Bountai to "PSL"Namark
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 6 | Pass | No | Bountai - Namark
2 | PDH |  |  |  | 6 | Pass | No | Bountai - Namark
3 | Free | 17.745 | 4.764 | 0.268 | 6 | Pass | No
4 | Free | 10.692 | 4.764 | 0.445 | 6 | Fail | 10.692
5 | Free | 17.745 | 4.764 | 0.268 | 6 | Pass | No
6 | Free | 17.745 | 4.764 | 0.268 | 6 | Pass | No
7 | Free | 17.745 | 7.935 | 0.238 | 6 | Pass | No
8 | Free | 1.249 | 0.266 | 0.212 | 6 | Fail | 1.249
9 | Free | 17.745 | 7.473 | 0.238 | 6 | Pass | No
10 | Free | 1.249 | 0.266 | 0.212 | 6 | Fail | 1.249
11 | STM-16 |  |  |  | 6 | Pass | No | Bountai - Namor
12 | STM-16 |  |  |  | 6 | Pass | No | Bountai - Namor
13 | Free | 10.337 | 2.026 | 0.195 | 6 | Fail | 10.337
14 | Free | 10.337 | 2.221 | 0.195 | 6 | Fail | 10.337
15 | Free | 3.574 | 0.796 | 0.221 | 6 | Fail | 3.574
16 | Free | 5.801 | 1.333 | 0.229 | 6 | Fail | 5.801
17 | RPT |  |  |  | 6 | Pass | No | Bountai - Nawai
18 | RPT |  |  |  | 6 | Pass | No | Bountai - Nawai
No.VII Mode: 18 Core From "PSL"Paknamnoy to "ODX"M. Lar
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 |  | 22.665 | 4.625 | 0.204 | 15 | Fail | 22.665
2 |  | 38.905 | 14.617 | 0.375 | 15 | Pass
3 |  | 38.905 | 13.787 | 0.354 | 15 | Pass
4 |  | 37.746 | 11.456 | 0.303 | 15 | Fail | 37.746
5 | RPT |  |  |  | 15 | Pass |  | RPT
6 | STM-4 |  |  |  | 15 | Pass |  | STM-4 ອຸດົມໄຊ
7 | STM-16 |  |  |  | 15 | Pass |  | STM-16 ອຸດົມໄຊ
8 |  | 34.991 |  |  | 15 | Fail
9 | STM-16 | 38.905 | 13.787 | 0.375 | 15 | Pass |  | STM-16 ອຸດົມໄຊ
10 | STM-4 | 38.905 | 13.787 | 0.375 | 15 | Pass |  | STM-4 ອຸດົມໄຊ
11 |  | 19.521 | 4.414 | 0.226 | 15 | Fail | 19.521 | _
12 |  | 35.854 | 13.093 | 0.365 | 15 | Pass | 35.854
13 |  | 19.521 | 4.414 | 0.226 | 15 | Fail | 19.521
14 |  | 14.157 | 2.759 | 0.194 | 15 | Fail | 14.157
15 |  | 14.157 | 2.804 | 0.198 | 15 | Fail | 14.157
16 |  | 19.521 | 4.398 | 0.225 | 15 | Fail | 19.521
17 |  | 14.157 | 2.863 | 0.202 | 15 | Fail | 14.157
18 |  | 14.157 | 3.182 | 0.224 | 15 | Fail | 14.157

## LPB
No.I Mode: 18 Core From "LPB"Phonpheng to "LPB"Xiengnguen
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 12 | Pass |  | BTS Nounsavath
2 | STM-64 |  |  |  | 12 | Pass |  | PP-Phoukhoun
3 | STM-64 |  |  |  | 12 | Pass |  | PP-Phoukhoun
4 | STM-1 |  |  |  | 12 | Pass |  | PP-xiengnguen
5 | STM-1 |  |  |  | 12 | Pass |  | PP-xiengnguen
6 | STM-64 |  |  |  | 12 | Pass |  | PP-Xayya
7 | PDH |  |  |  | 12 | Pass |  | BTS Km-10
8 | PDH |  |  |  | 12 | Pass |  | BTS Km-01
9 | PDH |  |  |  | 12 | Pass |  | BTS Km-01
10 | Media |  |  |  | 12 | Pass |  | DSLAM XiengNguen
11 | Media |  |  |  | 12 | Pass |  | DSLAM XiengNguen
12 | PDH |  |  |  | 12 | Pass |  | BTS Km-10
13 | Free | 5.05 | 1.76 | 0.34851 | 12 | Fail
14 | STM-64 |  |  |  | 12 | Pass |  | PP-Xayya
15 | PDH |  |  |  | 12 | Pass |  | BTS Kiewkacham
16 | PDH |  |  |  | 12 | Pass |  | BTS Kiewkacham
17 | Media |  |  |  | 12 | Pass |  | APB (LPB)
18 | Free | 23.65 | 9.35 | 0.39535 | 12 | Pass
No.II Mode: 24 Core From "LPB"Phonpheng to "LPB"Xiengnguen
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 10 | Pass |  | PP-Phoukhoun
2 | Free | 23.79 | 8.51 | 0.35771 | 10 | Pass
3 | Free | 23.79 | 8.91 | 0.37453 | 10 | Pass
4 | STM-64 |  |  |  | 10 | Pass |  | PP-Phoukhoun
5 | EDL Km-01 |  |  |  | 10 | Pass |  | PP-EDL Km-01
6 | PDH FE |  |  |  | 10 | Pass |  | 3G XiengNguen
7 | Free | 23.792 | 8.516 | 0.35794 | 10 | Pass
8 | Free | 23.79 | 8.918 | 0.37486 | 10 | Pass
9 | Free | 23.79 | 8.918 | 0.37486 | 10 | Pass
10 | Free | 23.79 | 8.919 | 0.37491 | 10 | Pass
11 | Free | 23.76 | 8.93 | 0.37584 | 10 | Pass
12 | Free | 23.76 | 8.08 | 0.34007 | 10 | Pass
13 | Free | 4.35 | 1.34 | 0.30805 | 10 | Fail
14 | Free | 23.76 | 8.09 | 0.34049 | 10 | Pass
15 | Free | 23.76 | 8.95 | 0.37668 | 10 | Pass
16 | Free | 23.76 | 8.65 | 0.36406 | 10 | Pass
17 | Free | 23.76 | 8.64 | 0.36364 | 10 | Pass
18 | Free | 23.76 | 8.65 | 0.36406 | 10 | Pass
19 | PDH |  |  |  | 10 | Pass |  | BTS Long Or
20 | PDH |  |  |  | 10 | Pass |  | BTS Long Or
21 | STM-64 |  |  |  | 10 | Pass |  | PP-NamThouam (EDL)
22 | STM-65 |  |  |  | 10 | Pass |  | PP-NamThouam (EDL)
23 |  | 7.61 | 2.58 | 0.33903 | 10 | Fail
24 |  | 7.62 | 2.59 | 0.3399 | 10 | Fail
No.III Mode: 18 Core From "LPB"Phonpheng to "LPB"Khokwa
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  | 2 | Pass |  | PP-Khokwa
2 | STM-1 |  |  |  | 2 | Pass |  | PP-Khokwa
3 | Free | 8.82 | 3.87 | 0.43878 | 2 | Pass
4 | Free | 8.11 | 3.16 | 0.38964 | 2 | Pass
5 | PDH |  |  |  | 2 | Pass |  | BTS Souphanouvong
6 | PDH |  |  |  | 2 | Pass |  | 3G Khokwa
7 | STM-16 |  |  |  | 2 | Pass |  | PP-Namthoum
8
9 | Free | 8.46 | 3.32 | 0.39243 | 2 | Pass
10 | Free | 8.56 | 3.04 | 0.35514 | 2 | Pass
11 | STM-16 |  |  |  | 2 | Pass |  | PP-Namthouam
12 | Free | 8.46 | 3.6 | 0.42553 | 2 | Pass
13 | PDH |  |  |  | 2 | Pass |  | BTS-PhouVao
14 | Media |  |  |  | 2 | Pass |  | Internet Phouvao Hotel
15 | Cell 3G |  |  |  | 2 | Pass |  | Phanom-Sangkhou
16 | LeasedLine |  |  |  | 2 | Pass |  | BOL(ທະນາຄານກາງ)
17 | Free | 3.98 | 1.03 | 0.25879 | 2 | Fail
18 | Free | 8.64 | 3.43 | 0.39699 | 2 | Pass
No.IV Mode: 24 Core From "LPB"PhonPheng to "LPB"KhokWa
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 2 |  |  | PP-Khokwa
2 | PDH |  |  |  | 2 |  |  | PP-Khokwa
3 | STM-16 |  |  |  | 2 |  |  | PP-Namthouam
4 | STM-16 |  |  |  | 2 |  |  | PP-Namthouam
5 | Free | 8.59 | 3.55 | 0.41327 | 2 | Pass
6 | PDH FE |  |  |  | 2 |  |  | PP-Souphanouvong
7 | Free | 8.59 | 3.55 | 0.41327 | 2 | Pass
8 | Free | 8.58 | 3.56 | 0.41492 | 2 | Pass
9 | Free | 8.59 | 3.45 | 0.40163 | 2 | Pass
10 | Free | 8.56 | 3.46 | 0.40421 | 2 | Pass
11 | Free | 8.58 | 3.54 | 0.41259 | 2 | Pass
12 | Free | 8.54 | 3.35 | 0.39227 | 2 | Pass
13 | PDH FE |  |  |  | 2 |  |  | PP-PakOu
14 | Free | 8.54 | 3.54 | 0.41452 | 2 | Pass
15 |  |  |  |  | 2
16 | Free | 8.15 | 3.65 | 0.44785 | 2 | Pass
17 | Free | 8.54 | 3.54 | 0.41452 | 2 | Pass
18 | Free | 8.58 | 4.03 | 0.4697 | 2 | Pass
19 | Free | 8.59 | 4.04 | 0.47031 | 2 | Pass
20 | Media Hotspot |  |  |  | 2 | Pass |  | PP-Souphanouvong
21 | Swich |  |  |  | 2 | Pass |  | PP-Khokwa
22 | Swich |  |  |  | 2 | Pass |  | PP-Khokwa
23 | PDH |  |  |  | 2 | Pass |  | BTS Phonsaat
24 | PDH |  |  |  | 2 | Pass |  | BTS Phonsaat
No.V Mode: 18 Core From "LPB"PakOu to "LPB" Namthoum.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 17.09 | 6.18 | 0.87 | 31 | Fail
2 | Free | 43.59 | 16.93 | 0.38 | 31 | Fail
3 | PDH |  |  |  | 31 | Pass |  | PakOu-Pakjeak
4 | PDH |  |  |  | 31 | Pass |  | PakOu-Pakjeak
5 | STM-16 |  |  |  | 31 | Pass |  | PP-Namthouam
6 | Free | 49.85 | 18.17 | 0.36 | 31 | Pass 71 |  | Spare PP-NT
7 | STM-1 |  |  |  | 31 | Pass |  | PakOu-NamThouam
8 | Free | 42.64 | 16.36 | 0,38 | 31 | Fail
9 | Free | 35.87 | 13.27 | 0,37 | 31 | Fail
10 | Free | 16.18 | 6.38 | 0,39 | 31 | Fail
11 | Cell 3G |  |  |  | 31 | Pass |  | PakOu-NamOu1
12 | Cell 2G |  |  |  | 31 | Pass |  | PakOu-NamOu2
13 | STM-1 |  |  |  | 31 | Pass |  | PakOu-Namthouam
14 | Free | 5,50 | 2,37 | 0,43 | 31 | Fail
15 | Free | 48,18 | 17,51 | 0,36 | 31 | Pass |  | Spare PP-NT
16 | STM-16 |  |  |  | 31 | Pass |  | PP-Namthouam
17 | Free | 38,41 | 14,61 | 0,38 | 31 | Fail
18 | Free | 5,54 | 2,18 | 0,39 | 31 | Fail
No.VIII Mode: 18 Core From "LPB"NamThouam to "LPB" Songja.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G | [6 empty] | NT-Nammong
2 | Free | 39,48 | 16,07 | 0,40 |  | Pass
3 | Free | 26,36 | 18,02 | 0,68 |  | Fail
4 | Free | 14,41 | 4,90 | 0,34 |  | Fail
5 | Free | 14,41 | 4,74 | 0,32 |  | Fail
6 | Free | 14.41 | 4,70 | 0,32 |  | Fail
7 | Free | 23,44 | 8,23 | 0,35 |  | Fail
8 | Free | 39,47 | 15,20 | 0,38 |  | Pass
9 | Free |  |  |  |  | Fail |  | ແທກບໍ່ອອກ
10 | Free | 39,49 | 14,86 | 0,37 |  | Pass
11 | Free | 35,27 | 16,58 | 0,47 |  | Fail
12 | Free | 39,48 | 16,02 | 0,40 |  | Pass
13 | PDH |  |  |  |  | Pass |  | BTS Songja
14 | STM-16 |  |  |  |  | Pass |  | NT-ODX
15 | PDH |  |  |  |  | Pass |  | BTS Songja
16 | STM-16 |  |  |  |  | Pass |  | NT-ODX
17 | Cell 3G |  |  |  |  | Pass |  | Pakbak-Pakmong
18 | Media |  |  |  |  | Pass |  | DSLAM Pakmong
No.IX Mode: 18 Core From "LPB"PakOu to "LPB" Khokwa.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | PakOu-Khokwa
2 | STM-1 |  |  |  |  | Pass |  | PakOu-Khokwa
3 | Free | 35,12 | 13,61 |  |  | Pass |  | Spare PP-NT
4 | Free | 14,39 | 4,98 |  |  | Fail
5 | Free | 35,09 | 15,78 |  |  | Pass |  | Spare PP-NT
6 | Free | 22,93 | 7,91 |  |  | Fail
7 | Cell2G |  |  |  |  | Pass |  | PakOu-Huiymard
8 | Cell2G |  |  |  |  | Pass |  | PakOu-Huiymard
9 | Free | 14,39 | 5,31 |  |  | Fail
10 | STM-16 |  |  |  |  | Pass |  | PP-NT
11 | STM-16 |  |  |  |  | Pass |  | PP-NT
12 | Free | 18,44 | 8,70 |  |  | Fail
13 | Free | 22,46 | 7,94 |  |  | Fail
14 | Free | 22,47 | 8,82 |  |  | Fail
15 | Free | 10,33 | 3,78 |  |  | Fail
16 | Free | 10,33 | 3,51 |  |  | Fail
17 | Free | 30,51 | 10,98 |  |  | Pass
18 | PDH |  |  |  |  | Pass |  | PakOu-PP
No.IX Mode: 18 Core From "LPB"Namthouam to "LPB" PakOu.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 31 | Pass |  | DSLAM NamOu2
2 | PDH |  |  |  | 31 | Pass |  | Xiengda
3 | PDH |  |  |  | 31 | Pass |  | BTS NamNga
4 | PDH |  |  |  | 31 | Pass |  | BTS NamNga
5 | Spare |  |  |  | 31 | Pass |  | NT-PP
6 | STM-16 |  |  |  | 31 | Pass |  | NT-PP
7 | STM-1 |  |  |  | 31 | Pass |  | NT-PakOu
8 | Cell 3G |  |  |  | 31 | Pass |  | Xiengda
9 | Media |  |  |  | 31 | Pass |  | BTS NamOu2
10 | PDH |  |  |  | 31 | Pass |  | BTS Donnguen
11 | Free | 33,95 | 13,60 | 0,40 | 31 | Fail
12 | Free | 33,95 | 13,01 | 0,38 | 31 | Fail
13 | STM-1 |  |  |  | 31 | Pass |  | NT-PakOu
14 | Free | 12,65 | 4,92 | 0,38 | 31 | Fail
15 | Cell 2G |  |  |  | 31 | Pass |  | Xiengda-ThaBoo
16 | STM-16 |  |  |  | 31 | Pass |  | NT-PP
17 | Free | 44,99 | 16,89 | 0,37 | 31 | Fail
18 | Cell 2G |  |  |  | 31 | Pass |  | Xiengda-ThaBoo
No.VIII Mode: 18 Core From "LPB"Namthouam "LPB" Nambark and Pakmong
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 HW |  |  |  | 11 | Pass |  | NT-PP
2 | STM-64 HW |  |  |  | 11 | Pass |  | NT-PP
3 | STM-64 HW |  |  |  | 11 | Pass |  | NT-ODX
4 | Free | 22,75 | 8,47 | 0,37 | 11 | Pass
5 | STM-64 HW |  |  |  | 11 | Pass |  | NT-ODX
6 | Free | 2,52 | 1,31 | 0,51 | 11 | Fail
7 | Cell 2G |  |  |  | 11 | Pass |  | Xiengda-Thaboo
8 | Cell 2G |  |  |  | 11 | Pass |  | Xiengda-Thaboo
9 | PDH |  |  |  | 11 | Pass |  | BTS Pakmong
10 | Free | 3,47 | 1,19 | 0,34 | 11 | Fail
11 | Free | 3,47 | 1,73 | 0,49 | 11 | Fail
12 | PDH |  |  |  | 11 | Pass |  | BTS Pakmong
13 | STM-4 |  |  |  | 11 | Pass |  | NT-M.Ngoy
14 | STM-4 |  |  |  | 11 | Pass |  | NT-M.Ngoy
15 | Cell 3G |  |  |  | 11 | Pass |  | Pakbak-Pakmong
16 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
17 | Media |  |  |  | 11 | Pass |  | DSLAM Nambark
18 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
No.XI Mode: 18 Core From "LPB"M. viengkham to "LPB" M. Viengthong.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Unitel |  |  |  | 80 |  |  | Unitel VK-VT
2 | Unitel |  |  |  | 80 |  |  | Unitel VK-VT
3 | Free | 14,29 | 6,51 | 0,45 | 80 | Fail
4 | PDH |  |  |  | 80 | Pass |  | Phousnam
5 | Free | 8,16 | 3,07 | 0,37 | 80 | Fail
6 | STM-4 |  |  |  | 80 | Pass |  | Viengkham-viengthong
7 | Cell 2G |  |  |  | 80 |  |  | Viengkham-Sobhuerng
8 | PDH |  |  |  | 80 | Pass |  | Phousnam
9 | Free | 8,20 | 3,10 | 0,37 | 80 | Fail
10 |  |  |  |  | 80 |  |  | ແທກບໍ່ອອກ
11 | Free | 8,26 | 3,41 | 0,41 | 80 | Fail
12 | Free | 20,75 | 10,60 | 0,51 | 80 | Fail
13 | PDH |  |  |  | 80 |  |  | BTS Huiychorc
14 | Free | 18,37 | 6,78 | 0,36 | 80 | Fail
15 | Free | 8,66 | 3,25 | 0,37 | 80 | Fail
16 | PDH |  |  |  | 80 |  |  | BTS Huiychorc
17 | Free | 41,99 | 16,86 | 0,40 | 80 | Fail
18 | STM-4 |  |  |  | 80 | Pass |  | Viengkham-viengthong
No.XI Mode: 18 Core From "LPB"M.Ngoy to "LPB" M. Viengkham.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G |  |  |  | 49 | Pass |  | Nongkhiew-pakbak
2 | Cell 2G |  |  |  | 49 | Pass |  | Nongkhiew-pakbak
3 | Media |  |  |  | 49 | Pass |  | Leased line BCEL
4 | Free | 13,65 | 4,83 | 0,35 | 49 | Fail
5 | STM-4 |  |  |  | 49 | Pass |  | M.ngoy-M.Viengkham
6 | Free | 53,33 | 17,08 | 0,32 | 49 | Pass |  | Spare
7 | STM-4 |  |  |  | 49 | Pass |  | M.ngoy-M.Viengkham
8 | PDH |  |  |  | 49 | Pass |  | BTS Phoutidphuerng
9 | PDH |  |  |  | 49 | Pass |  | BTS Phoutidphuerng
10 | Media |  |  |  | 49 | Pass |  | DSLAM Nongkheiw
11 | Cell 3G |  |  |  | 49 | Pass |  | Pakbak-Nongkheiw
12 | Cell 3G |  |  |  | 49 | Pass |  | Pakbak-Nongkheiw
13 | Free | 24,53 | 8,46 | 0,34 | 49 | Fail
14 | PDH |  |  |  | 49 | Pass |  | BTS Nongkheiw
15 | Free | 4,27 | 1,44 | 0,33 | 49 | Fail
16 | Repeator |  |  |  | 49 | Pass |  | NongEain
17 | PDH |  |  |  | 49 | Pass |  | BTS Nongkheiw
18 | Free | 4,27 | 1,48 | 0,34 | 49 | Fail
No.XI Mode: 18 Core From "LPB"M.Ngoy to "LPB" M. Nambark.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 8 | Pass |  | BTS B. Lee
2 | Free | 14,82 | 5,65 | 0,38 | 8 | Fail
3 | PDH |  |  |  | 8 | Pass |  | BTS B. Lee
4 | Cell 3G |  |  |  | 8 | Pass |  | Pakmong
5 | Cell 3G |  |  |  | 8 | Pass |  | Nambark
6 | STM-4 |  |  |  | 8 | Pass |  | M.Ngoy-Namthouam
7 | Cell 3G |  |  |  | 8 | Pass |  | Nambark
8 | STM-4 |  |  |  | 8 |  |  | M.Ngoy-Namthouam
No.XI Mode: 18 Core From "LPB" Nambark to "LPB" M. Ngoy.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-4 |  |  |  | 8 | Pass |  | NT-M. Ngoy
2 | Cell 3G |  |  |  | 8 | Pass |  | M.Ngoy-Nambark
3 | Cell 3G |  |  |  | 8 | Pass |  | M.Ngoy-Pakmong
4 | Free | 7,64 | 4,56 | 0,59 | 8 | Fail
5 | Free | 2,97 | 1,07 | 0,36 | 8 | Fail
6 | Free | 2,97 | 1,13 | 0,38 | 8 | Fail
7 | STM-4 |  |  |  | 8 |  |  | NT-M. Ngoy
8 | Cell 3G |  |  |  | 8 | Pass |  | M.Ngoy-Nambark
No.XI Mode: 18 Core From "LPB" Nambark to "LPB" Namthouam.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-4 |  |  |  | 11 | Pass |  | NT-M. Ngoy
2 | Cell 3G |  |  |  | 11 | Pass |  | M.Ngoy-Nambark
3 | Media |  |  |  | 11 | Pass |  | Internet Nambark
4 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
5 | Free | 19,28 | 6,95 | 0,36 | 11 | Fail
6 | Free | 22,75 | 8,39 | 0,36 | 11 | Pass
7 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
8 | Cell 3G |  |  |  | 11 | Pass |  | M.Ngoy-Pakmong
No.X Mode: 18 Core From "LPB"Songja "LPB" Namthouam
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 19.63 | 8.79 |  | 37 | Fail
2 | Free | 39,48 | 14,87 |  | 37 | Pass
3 | Free | 19,63 | 11,06 |  | 37 | Fail
4 | Free | 25,09 | 10,97 |  | 37 | Fail
5 | Free | 25,09 | 12,75 |  | 37 | Fail
6 | Free | 25,08 | 11,08 |  | 37 | Fail
7 | Free | 16,05 | 8,05 |  | 37 | Fail
8 |  |  |  |  | 37 |  |  | ຕໍ່ຜ່ານ
9 | Free | 39,48 | 16,24 |  | 37 | Pass
10 | Free | 39,49 | 15,19 |  | 37 | Fail
11 |  |  |  |  | 37 |  |  | ຕໍ່ຜ່ານ
12 |  |  |  |  | 37 |  |  | ແທກບໍ່ອອກ
13 | PDH |  |  |  | 37 | Pass |  | BTS SongJa
14 | STM-16 |  |  |  | 37 | Pass |  | Namthouam-ODX
15 | STM-16 |  |  |  | 37 | Pass |  | Namthouam-ODX
16 | PDH |  |  |  | 37 | Pass |  | BTS SongJa
17 | Repeator |  |  |  | 37 | Pass |  | KaJet
18 | Free | 12,60 | 5,74 |  | 37 | Fail
No.X Mode: 18 Core From "LPB"Songja "ODX" Oudomxay.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 13,85 | 5,68 |  |  | Fail
2 | STM-64 | [6 empty] | NT-ODX
3 | Free | 13,85 | 5,46 |  |  | Fail
4 | Free | 13,85 | 5,54 |  |  | Fail
5 | STM-64 | [6 empty] | NT-ODX
6 | Free | 13,85 | 5,02 |  |  | Fail
7 | Free | 14,56 | 5,83 |  |  | Fail
8 | Free | 6,32 | 3,08 |  |  | Fail
9 | Free | 6,32 | 2,81 |  |  | Fail
10 | Free | 14,65 | 6,57 |  |  | Fail
11 | Free | 40,00 | 15,62 |  |  | Pass
12 | Free | 39,47 | 15,91 |  |  | Fail
13 | Free | 14,66 | 5,79 |  |  | Fail
14 | Free | 3,88 | 1,39 |  |  | Fail
15 | Free | 14,66 | 6,90 |  |  | Fail
16 | Free | 14,65 | 5,90 |  |  | Fail
17 | Repeator | [6 empty] | Pungving
18 | Free | 13,85 | 5,83 |  |  | Fail
No.X Mode: 18 Core From "LPB"Keiwkacham "LPB" XiengNguen.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 44 | Pass |  | PP-Phoukhoun
2 | Free | 49,55 | 21,45 |  | 44 | Pass
3 | Free | 49,,56 | 22,54 |  | 44 | Pass
4 | Free | 49,34 | 21,65 |  | 44 | Pass
5 | Repeator | 23,13 | 9,09 |  | 44 | Pass |  | Keiwkacham-Namming
6 | Repeator | 23,12 | 11,41 |  | 44 | Pass |  | Keiwkacham-Namming
7 | Free | 43,22 | 18,66 |  | 44 | Fail
8 | Free | 17,47 | 7,41 |  | 44 | Fail
9 | Free | 11,56 | 4,47 |  | 44 | Fail
10 | Free | 11,57 | 4,70 |  | 44 | Fail
11 | Free | 11,57 | 4,50 |  | 44 | Fail
12 | Free | 11,57 | 4,54 |  | 44 | Fail
13 | PDH |  |  |  | 44 | Pass |  | BTS keiwkacham
14 | PDH |  |  |  | 44 | Pass |  | BTS keiwkacham
15 | STM-64 |  |  |  | 44 | Pass |  | PP-Phoukhoun
16 | Free | 45,77 | 17,78 |  | 44 | Fail
17 | Free | 34,72 | 16,69 |  | 44 | Fail
18 | Free | 40,13 | 14,94 |  | 44 | Fail
No.X Mode: 18 Core From "LPB"Keiwkacham "LPB" Phoukoun.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  |  | Pass |  | PP-Phoukhoun
2 | STM-64 |  |  |  |  | Pass |  | PP-Phoukhoun
3 | Free | 19,23 | 7,28 |  |  | Fail
4 | Free | 19,23 | 7,28 |  |  | Fail
5 | Free | 32,96 | 17,06 |  |  | Fail |  | ຜ່ານແຕ່ມີ Loss ສູງ
6 |  | 39,30 | 17,59 |  |  | Fail |  | ຜ່ານແຕ່ມີ Loss ສູງ
7 | Free | 18,28 | 7,12 |  |  | Fail
8 | Free | 18,28 | 8,46 |  |  | Fail
9 | Free | 18,28 | 7,39 |  |  | Fail
10 | Free | 18,28 | 6,75 |  |  | Fail
11 | Free | 18,28 | 7,13 |  |  | Fail
12 | Free | 18,29 | 7,14 |  |  | Fail
13 | Free | 48,86 | 18,81 |  |  | Pass
14 | Free | [6 empty] | ແທກບໍ່ອອກ
15 | Free | 48,93 | 17,65 |  |  | Pass
16 | Free | 17,24 | 6,45 |  |  | Fail
17 | Repeator |  |  |  |  | Pass |  | Kiewkacham-NongOun
18 | Free | 21,51 | 9,36 |  |  | Fail
No.X Mode: 18 Core From "LPB"PhouKoun "LPB"Keiwkacham .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 41 | Pass |  | Phoukhoun-PP
2 | STM-64 |  |  |  | 41 | Pass |  | Phoukhoun-PP
3 | Free | 8,66 | 4,84 |  | 41 | Fail
4 | Free | 29,73 | 11,71 |  | 41 | Fail
5 | Free | 33,62 | 17,50 |  | 41 | Fail
6 | Free | 29,68 | 1,72 |  | 41 | Fail
7 | Free | 9,70 | 3,73 |  | 41 | Fail
8 | Free | 30,63 | 12,84 |  | 41 | Fail
9 | Free | 30,63 | 14,91 |  | 41
10 | PDH |  |  |  | 41 | Pass |  | BTS Phakiengnoy
11 | Free | 30,64 | 12,47 |  | 41
12 | PDH |  |  |  | 41 | Pass |  | BTS Phakiengnoy
13 | Free | 48,86 | 18,81 |  | 41 | Pass
14 | Free | 48,87 | 18,82 |  | 41 | Pass
15 | Free | 48,86 | 18,73 |  | 41 | Pass
16 | Free | 17,19 | 8,30 |  | 41 | Fail
17 | Free | 17,66 | 8,11 |  | 41 | Fail
18 | Free | 11,79 | 4,66 |  | 41 | Fail
No.X Mode: 18 Core From "LPB"Phoukoun "Kasi" Kasi
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | PK-Kasi
2 | Free | 4,76 | 1,65 |  |  | Fail
3 | Free | 42,13 | 16,16 |  |  | Pass
4 | STM-1 |  |  |  |  | Pass |  | PK-Kasi
5 | STM-64 |  |  |  |  | Pass |  | PK-Kasi
6 | STM-64 |  |  |  |  | Pass |  | PK-Kasi
7 | Free | 13,95 | 5,34 |  |  | Fail
8 | Free | 37,64 | 14,91 |  |  | Fail
9 | Free | 23,28 | 9,08 |  |  | Fail
10 | Free | 23,05 | 9,37 |  |  | Fail
11 | Free | 13,95 | 5,71 |  |  | Fail
12 | Free | 3,95 | 5,46 |  |  | Fail
13 | Free | 10,86 | 4,41 |  |  | Fail
14 | Free | 6,44 | 2,72 |  |  | Fail
15 | Free | 13,21 | 6,72 |  |  | Fail
16 | Free | 13,21 | 5,09 |  |  | Fail
17 | Free | 13,22 | 6,23 |  |  | Fail
18 | Free | 13,21 | 6,01
No.X Mode: 18 Core From "LPB"Phoukhoun "LPB" XiengKhouang.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-16 |  |  |  |  | Pass |  | Phoukoun-Xiengkhouang
2 | STM-16 |  |  |  |  | Pass |  | Phoukoun-Xiengkhouang
3 | PDH |  |  |  |  | Pass |  | BTS Phousong
4 | Free | 6,51 | 3,32 |  |  | Fail
5 | PDH |  |  |  |  | Pass |  | BTS Phousong
6 | Free | 45,37 | 17,77 |  |  | Fail
7 | Free | 42,56 | 16,97 |  |  | Fail
8 | Free | 46,01 | 18,17 |  |  | Fail
9 | Free | 46,81 | 18,09 |  |  | Fail
10 | Free | 43,09 | 17,53 |  |  | Fail
11 | PDH |  |  |  |  | Pass |  | PK-NamNguerm 5
12 | PDH |  |  |  |  | Pass |  | PK-NamNguerm 6
13
14
15
16
17
18
No.X Mode: 18 Core From "LPB"XiengNguen "LPB" Phonpheng.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free |  |  |  |  | Fail |  | ແທກບໍ່ອອກ
2 | STM-64 |  |  |  |  | Pass |  | PP-Phoukhoun
3 | STM-64 |  |  |  |  | Pass |  | PP-Phoukhoun
4 | STM-1 |  |  |  |  | Pass |  | xiengNguen-PP
5 | STM-1 |  |  |  |  | Pass |  | xiengNguen-PP
6 | STM-64 |  |  |  |  | Pass |  | PP-Xayya
7 | Free | 11,86 | 4,56 |  |  | Fail
8 | Free | 18,06 | 6,18 |  |  | Fail
9 | Free | 18,06 | 6,16 |  |  | Fail
10 | Media |  |  |  |  | Pass |  | DSLAM XiengNguen
11 | Media |  |  |  |  | Pass |  | DSLAM XiengNguen
12 | Free | 16,51 | 5,75 |  |  | Fail
13 | Free | 15,07 | 5,12 |  |  | Fail
14 | STM-64 |  |  |  |  | Pass |  | PP-Xayya
15 | PDH | [6 empty] | PP-Kiewkacham
16 | PDH | [6 empty] | PP-Kiewkacham
17 | Free | 21,04 | 7,23 |  |  | Fail
18 | Free | 21,03 | 7,24 |  |  | Fail
No.X Mode: 24 Core From "LPB"XiengNguen "LPB" Phonpheng.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  |  | Pass |  | PP-B.Dan
2 | Free | 23,79 | 8,68 |  |  | Pass
3 | Free | 23,79 | 9,35 |  |  | Pass
4 | STM-64 |  |  |  |  | Pass |  | PP-B.Dan
5 | Free | 20,40 | 9,57 |  |  | Fail
6 | S |  |  |  |  | Pass |  | PP-XiengNguen
7 | Spare |  |  |  |  | Pass |  | PP-kiewkacham
8 | Spare |  |  |  |  | Pass |  | PP-kiewkacham
9 | Free | 23,97 | 8,53 |  |  | Pass
10 | Free | 23,97 | 8,65 |  |  | Pass
11 | Free | 23,64 | 9,06 |  |  | Pass
12 | Free | 23,76 | 8,71 |  |  | Pass
13 | Free | 20,4 | 7,87 |  |  | Fail
14 | Free | 23,76 | 10,10 |  |  | Pass
15 | Free | 23,76 | 9,46 |  |  | Pass
16 | Free | 23,76 | 9,34 |  |  | Pass
17 | Free | 23,76 | 8,81 |  |  | Pass
18 | Free | 23,75 | 9,03 |  |  | Pass
19 | Free | 14,83 | 5,64 |  |  | Pass
20 | Free | 14,82 | 5,28 |  |  | Pass
21 | Free | 7.56 | 2.7 |  |  | Pass
22 | Free | [6 empty] | ແທກບໍ່ອອກ
23 | Free | 9.11 | 3.38 |  |  | pass
24 | Free | 16,34 | 6,65 |  |  | pass
No.X Mode: 18 Core From "LPB"XiengNguen "LPB" Kiewkacham.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM -64 |  |  |  |  | Pass |  | PP-Phoukhoun
2 | Free | 49,55 | 18,64 |  |  | Pass
3 | Spare |  |  |  |  | Pass |  | PP-Phoukhoun
4 | Spare |  |  |  |  | Pass |  | PP-Phoukhoun
5 | Free | 27,63 | 10,27 |  |  | Fail
6 | Free | 27,37 | 10,82 |  |  | Fail
7 | PDH |  |  |  |  | Pass |  | BTS Namkhan 3
8 | PDH |  |  |  |  | Pass |  | BTS Namkhan 4
9 | Cell 3G |  |  |  |  | Pass |  | Namkhan3
10 | Free | 37,96 | 15,22 |  |  | Pass
11 | Free | 37,92 | 15,87 |  |  | Fail
12 | Free | 37,98 | 15,14 |  |  | Fail
13 | PDH |  |  |  |  | Pass |  | PP-Keiwkacham
14 | PDH |  |  |  |  | Pass |  | PP-Keiwkacham
15 | STM -64 |  |  |  |  | Pass |  | PP-Phoukhoun
16 | Free | 2,17 | 1,03 |  |  | Fail
17 | Free | 49,78 | 19,34 |  |  | Pass
18 | Free | 49,79 | 19,35 |  |  | Pass
No.X Mode: 18 Core From "LPB"XiengNguen "LPB" B Dan.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 23,06 | 9,07 |  |  | Fail
2 | Free | 24,79 | 10,40 |  |  | Pass
3 | STM-64 |  |  |  |  | Pass |  | PP-B.Dan
4 | STM-64 |  |  |  |  | Pass |  | PP-B.Dan
5 | Free | 23,60 | 9,60 |  |  | Fail
6 | Free | 24,78 | 10,90 |  |  | Pass
7 | PDH |  |  |  |  | Pass |  | BTS Slalek
8 | Free | 12,87 | 5,04 |  |  | Fail
9 | Free | 12,88 | 5,05 |  |  | Fail
10 | Free | 23,60 | 9,71 |  |  | Fail
11 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
12 | Free | 32,45 | 14,06 |  |  | Pass
13 | Free | [6 empty] | ແທກບໍ່ອອກ
14 | PDH |  |  |  |  | Pass |  | BTS Silalek
15 | STM-64 |  |  |  |  | Pass |  | PP-Xayya
16 | Media |  |  |  |  | Pass |  | Internet Huiykod
17 | STM-64 |  |  |  |  | Pass |  | PP-Xayya
18 | STM-1 |  |  |  |  | Pass |  | PP-M.Nan
No.X Mode: 18 Core From "LPB"B.Dan "LPB"XiengNguen .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 2,43 | 2,10 |  |  | Fail
2 | Free | 10,53 | 5,53 |  |  | Fail
3 | STM-64 |  |  |  |  | Pass |  | B.Dan-PP
4 | STM-64 |  |  |  |  | Pass |  | B.Dan-PP
5 | PDH |  |  |  |  | Pass |  | B.Dan-Silalek
6 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayyya
7 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayyya
8 | Free | 10,53 | 5,87 |  |  | Fail
9 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
10 | Free | 12,26 | 6,71 |  |  | Fail
11 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
12 | PDH |  |  |  |  | Pass |  | B.Dan-Silalek
13 | Free | 10,54 | 5,12 |  |  | Fail
14 | Free | 10,53 | 5,89 |  |  | Fail
15 | Free | 10,53 | 8,34 |  |  | Fail
16 | Free | 4,76 | 2,26 |  |  | Fail
17 | Free | 34,45 | 17,20 |  |  | Pass
18 | Free | 34,32 | 17,87 |  |  | Pass
No.X Mode: 18 Core From "LPB"B.Dan "LPB"M. Nan .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 6,69 | 2,63 |  |  | Fail
2 | Free | 6,74 | 2,68 |  |  | Fail
3 | Free | 6,71 | 2,69 |  |  | Fail
4 | Free | 6,78 | 2,66 |  |  | Fail
5 | Free | 6,71 | 2,65 |  |  | Fail
6 | Free | 6,74 | 2,68 |  |  | Fail
7 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
8 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
9 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
10 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
11 | Free | 2,23 | 1,02 |  |  | Fail
12 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
13 | Free | 4,80 | 2,65 |  |  | Fail
14 | PDH |  |  |  |  | Pass |  | B.Dan-Phousacan
15 | PDH |  |  |  |  | Pass |  | B.Dan-Phousacan
16 | Free | 12,07 | 3,63 |  |  | Fail
17 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
18 | Free | 12,07 | 3,87 |  |  | Fail
No.X Mode: 18 Core From "LPB"M.Nan "LPB"B.Dan .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G |  |  |  |  | Pass |  | Nalao
2 | Cell 2G |  |  |  |  | Pass |  | Nalao
3 | Free | 8,22 | 3,31 |  |  | Fail
4 | [7 empty] | ຕໍ່ຜ່ານ
5 | Free | 8,22 | 3,22 |  |  | Fail
6 | Free | 6,74 | 2,68 |  |  | Fail
7 | STM-1 |  |  |  |  | Pass |  | M.Nan-XiengNguen
8 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
9 | STM-1 |  |  |  |  | Pass |  | M.Nan-XiengNguen
10 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
11 | Free | 8,22 | 3,29 |  |  | Fail
12 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
13 | PDH |  |  |  |  | Pass |  | M.Nan-Phousacan
14 | PDH |  |  |  |  | Pass |  | M.Nan-Phousacan
15 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
16 | [7 empty] | ຕໍ່ຜ່ານ
17 | Media |  |  |  |  | Pass |  | Leased Line LDB M.Nan
18 | Cell 2G |  |  |  |  | Pass |  | Keomany
No.X Mode: 18 Core From "LPB"M.Nan "XLY"Sayyabouly .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | M.Nan-Xayya
2 | Free | 8,77 | 2,79 |  |  | Pass |  | ThaDuer XYL
3 | STM-1 |  |  |  |  | Pass |  | M.Nan-Xayya
4 | 8,77 | 3,04 |  |  |  | Pass |  | ThaDuer XYL
5 | Free | 8,77 | 3,26 |  |  | Pass |  | ThaDuer XYL
6 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
7 | Free | 8,77 | 3,32 |  |  | Pass |  | ThaDuer XYL
8 | Free | 8,77 | 3,00 |  |  | Pass |  | ThaDuer XYL
9 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
10 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
11 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
12 | [7 empty] | ຕໍ່ຜ່ານ
13 | [7 empty] | ຕໍ່ຜ່ານ
14 | Free | 8,78 | 3,03 |  |  | Pass |  | ThaDuer XYL
15 | Free | 8,77 | 3,15 |  |  | Pass |  | ThaDuer XYL
16 | Free | 8,77 | 3.21 |  |  | Pass |  | ThaDuer XYL
17 | Free | 5,14 | 1,75 |  |  | Fail
18 | Free | 5,14 | 1,78 |  |  | Fail
No.II Mode: 24 Core From "LPB"Khokwa to "LPB"Phonpheng
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  |  | Pass |  | Khokwa-PP
2 | PDH |  |  |  |  | Pass |  | Khokwa-PP
3 | STM-16 |  |  |  |  | Pass |  | PP-NT
4 | STM-16 |  |  |  |  | Pass |  | PP-NT
5 | PDH |  |  |  |  | Pass |  | Khokwa-Airport
6 | Free | 4,55 | 1,58 |  |  | Fail
7 | Free | 8,55 | 3,14 |  |  | Pass
8 | Free | 8,58 | 3,12 |  |  | Pass
9 | Free | 8,55 | 3,28 |  |  | Pass
10 | Free | 8,58 | 2,97 |  |  | Pass
11 | Free | 8,55 | 3,06 |  |  | Pass
12 | Free | 8,58 | 3,08 |  |  | Pass
13 | PDH |  |  |  |  | Pass |  | PP-PakOu
14 | PDH |  |  |  |  | Pass |  | Khokwa-Airport
15 | Free | 8,57 | 2,93 |  |  | Pass
16 | Free | 0,42 | 0,18 |  |  | Fail
17 | Free | 8,58 | 3,16 |  |  | Pass
18 | Free | 8,58 | 3,15 |  |  | Pass
19 | Free | 8,58 | 3,06 |  |  | Pass
20 | Internet Hotspot |  |  |  |  | Pass |  | PP-Souphanouvong
21 | Swich |  |  |  |  | Pass |  | PP-KhokWa
22 | Swich |  |  |  |  | Pass |  | PP-KhokWa
23 | Free | 2,84 | 5,29 |  |  | Fail
24 | Free | 2,84 | 1,09 |  |  | Fail
No.X Mode: 18 Core From "LPB"Khokwa"LPB"Phonpheng .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | PP-Khokwa
2 | STM-1 |  |  |  |  | Pass |  | PP-Khokwa
3 | Free | 8,47 | 3,99 |  |  | Pass
4 | Free | 8,45 | 4,20 |  |  | Pass
5 | PDH |  |  |  |  | Pass |  | BTS Souphanouvong
6 | PDH |  |  |  |  | Pass |  | 3G Khokwa
7 | [7 empty] | ບໍ່ໄດ້ຕໍ່ອອກ ODF
8 | [7 empty] | ບໍ່ໄດ້ຕໍ່ອອກ ODF
9 | ຕໍ່ຜ່ານ | [6 empty] | ຕໍ່ໃສ່ Core11-PakOu
10 | ຕໍ່ຜ່ານ | [6 empty] | ຕໍ່ໃສ່ Core12-PakOu
11 | [7 empty] | ບໍ່ໄດ້ຕໍ່ອອກ ODF
12 | Free | 8,46 | 3,51 |  |  | Pass
13 | Free | 1,22 | 2,32 |  |  | Fail
14 | [5 empty] | Pass |  | ຕໍ່ຜ່ານໄປປາກອູ
15 | [5 empty] | Pass |  | ຕໍ່ຜ່ານໄປປາກອູ
16 | Free | 7.34 | 2.73 |  |  | Fail
17 | PDH |  |  |  |  | Fail |  | PP-Airport
18 | Free | 3,86 | 1,28 |  |  | Fail
No.II Mode: 18 Core From "LPB"Khokwa to "LPB"PakOu.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | Khokwa-PP
2 | STM-1 |  |  |  |  | Pass |  | Khokwa-PP
3 | Free | 26,64 | 10,24 |  |  | Pass
4 | Cell 3G | [6 empty] | Paksuerng
5 | FTTH | [6 empty] | B-sandsook
6 | ຕໍ່ຜ່ານ | [6 empty] | PP-PakOu
7 | Internet Hotspot | [6 empty] | PP-Souphanouvong
8 | PDH |  |  |  |  | Pass |  | BTS Paksuerng
9 | PDH FE |  |  |  |  | Pass |  | PP-Souphanouvong
10 | STM-16 |  |  |  |  | Pass |  | PP-NT
11 | STM-16 |  |  |  |  | Pass |  | PP-NT
12 | Spare | [6 empty] | PP-NT
13 | Free | 5,48 | 4,86 |  |  | Fail
14 | Media |  |  |  |  | Pass |  | DSLAM Souphanouvong
15 | Free | 18,29 | 9,33 |  |  | Fail
16 | PDH FE | [6 empty] | Outdoor Kaset Paksuerng
17 | Free | 26,64 | 9.55 |  |  | Pass
18 | PDH FE | [6 empty] | PP-PakOu

## Sheet1
ແຜນການເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
ລ/ດ | ສະຖານີຕົ້ນທາງ | ສະຖານີປາຍທາງ | ໝາຍເຫດ
1 | ໂພນແພງ | ຄົກວ່າ | ມີສາຍສອງເສັ້ນ 18 Core ແລະ 24
2 | ຄົກວ່າ | ປາກອູ
3 | ປາກອູ | ນໍ້າຖ້ວມ
4 | ນໍ້າຖ້ວມ | ປາກມອງ
5 | ນໍ້າຖ້ວມ | ຊົ່ງຈ່າ
6 | ປາກມອງ | ນໍ້າບາກ
7 | ນໍ້າບາກ | ເມືອງງອຍ
8 | ເມືອງງອຍ | ເມືອງວຽງຄຳ
9 | ເມືອງວຽງຄຳ | ເມືອງວຽງທອງ
10 | ໂພນແພງ | ເມືອງຊຽງເງິນ | ມີສາຍສອງເສັ້ນ 18 Core ແລະ 24
11 | ເມືອງຊຽງເງິນ | ກີ່ວກະຈຳ
12 | ກີ່ວກະຈຳ | ພູຄູນ
13 | ເມືອງຊຽງເງິນ | ສີລາເລກ
14 | ສີລາເລກ | ບ້ານດ່ານ
15 | ບ້ານດ່ານ | ພູສະແກນ
16 | ພູສະແກນ | ເມືອງນານ
17 | ເມືອງນານ | ໄຊຍະ

## Core Optic LPB 23-04-17
No.I Mode: 18 Core From "LPB"Phonpheng to "LPB"Xiengnguen
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 12 | Pass |  | BTS Nounsavath
2 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Phoukhoun
3 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Phoukhoun
4 | STM-1 |  |  |  | 12 | Pass | STM-1 | PP-xiengnguen
5 | STM-1 |  |  |  | 12 | Pass | STM-1 | PP-xiengnguen
6 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Xayya
7 | PDH |  |  |  | 12 | Pass | 11.86 | BTS Km-10
8 | PDH |  |  |  | 12 | Pass | 18.06 | BTS Km-01
9 | PDH |  |  |  | 12 | Pass | 18.06 | BTS Km-01
10 | Media |  |  |  | 12 | Pass | Media | DSLAM XiengNguen
11 | Media |  |  |  | 12 | Pass | Media | DSLAM XiengNguen
12 | PDH |  |  |  | 12 | Pass | 16.51 | BTS Km-10
13 | Free | 5.05 | 1,76 | 0,34 | 12 | Fail | 15,07
14 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Xayya
15 | PDH |  |  |  | 12 | Pass | PDH | BTS Kiewkacham
16 | PDH |  |  |  | 12 | Pass | PDH | BTS Kiewkacham
17 | Media |  |  |  | 12 | Pass | 21.04 | APB (LPB)
18 | Media |  |  |  | 12 | Pass | 21.03 | APB (LPB)
No.II Mode: 24 Core From "LPB"Phonpheng to "LPB"Xiengnguen
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 10 | Pass | STM-64 | PP-Phoukhoun
2 | Free | 23.792 | 8.515 | 0.35789 | 10 | Pass | 23.792
3 | Free | 23.793 | 8.918 | 0.37482 | 10 | Pass | 23.793
4 | STM-64 |  |  |  | 10 | Pass | STM-64 | PP-Phoukhoun
5 | EDL Km-01 |  |  |  | 10 | Pass | 20,40 | PP-EDL Km-01
6 | PDH FE |  |  |  | 10 | Pass | PDH FE | 3G XiengNguen
7 | Free | 23.792 | 8.516 | 0.35794 | 10 | Pass | 23.792
8 | Free | 23.79 | 8.918 | 0.37486 | 10 | Pass | 23.79
9 | Free | 23.79 | 8.918 | 0.37486 | 10 | Pass | 23.79
10 | Free | 23.79 | 8.919 | 0.37491 | 10 | Pass | 23.79
11 | Free | 23.76 | 8.93 | 0.37584 | 10 | Pass | 23.76
12 | Free | 23.76 | 8.08 | 0.34007 | 10 | Pass | 23.76
13 | Free | 4.35 | 1.34 | 0.30805 | 10 | Fail | 20,40
14 | Free | 23.76 | 8.09 | 0.34049 | 10 | Pass | 23.76
15 | Free | 23.76 | 8.95 | 0.37668 | 10 | Pass | 23.76
16 | Free | 23.76 | 8.65 | 0.36406 | 10 | Pass | 23.76
17 | Free | 23.76 | 8.64 | 0.36364 | 10 | Pass | 23.76
18 | Free | 23.76 | 8.65 | 0.36406 | 10 | Pass | 23.76
19 | PDH |  |  |  | 10 | Pass | 14.83 | BTS Long Or
20 | PDH |  |  |  | 10 | Pass | 14.82 | BTS Long Or
21 | STM-64 |  |  |  | 10 | Pass | 7.56 | PP-NamThouam (EDL)
22 | STM-64 |  |  |  | 10 | Pass | ແທກບໍ່ອອກ | PP-NamThouam (EDL)
23 |  | 7.61 | 2.58 | 0.33903 | 10 | Fail | 9,11
24 |  | 7.62 | 2.59 | 0.3399 | 10 | Fail | 16,34
No.III Mode: 18 Core From "LPB"Phonpheng to "LPB"Khokwa
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  | 2 | Pass | STM-1 | PP-Khokwa
2 | STM-1 |  |  |  | 2 | Pass | STM-1 | PP-Khokwa
3 | Free | 8.82 | 3.87 | 0.43878 | 2 | Pass | 8.82
4 | Free | 8.11 | 3.16 | 0.38964 | 2 | Pass | 8.11
5 | PDH |  |  |  | 2 | Pass | PDH | BTS Souphanouvong
6 | PDH |  |  |  | 2 | Pass | PDH | 3G Khokwa
7 | STM-16 |  |  |  | 2 | Pass | STM-16 | PP-Namthoum
8
9 | Free | 8.46 | 3.32 | 0.39243 | 2 | Pass | 8.46
10 | Free | 8.56 | 3.04 | 0.35514 | 2 | Pass | 8.56
11 | STM-16 |  |  |  | 2 | Pass | STM-16 | PP-Namthouam
12 | Free | 8.46 | 3.6 | 0.42553 | 2 | Pass | 8.46
13 | PDH |  |  |  | 2 | Pass | 1,22 | BTS-PhouVao
14 | Media |  |  |  | 2 | Pass |  | Internet Phouvao Hotel
15 | Cell 3G |  |  |  | 2 | Pass |  | Phanom-Sangkhou
16 | LeasedLine |  |  |  | 2 | Pass | 7,34 | BOL(ທະນາຄານກາງ)
17 | Free | 3.98 | 1.03 | 0.25879 | 2 | Fail | PDH Airport
18 | Free | 8.64 | 3.43 | 0.39699 | 2 | Pass
No.II Mode: 24 Core From "LPB"Khokwa to "LPB"Phonpheng
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 2 | Pass | PDH | Khokwa-PP
2 | PDH |  |  |  | 2 | Pass | PDH | Khokwa-PP
3 | STM-16 |  |  |  | 2 | Pass | STM-16 | PP-NT
4 | STM-16 |  |  |  | 2 | Pass | STM-16 | PP-NT
5 | Free | 8.55 | 3.14 | 0.36725 | 2 | Pass | 8,55
6 | PDH |  |  |  | 2 | Pass | PDH Souphanouvong | Souphanouvong
7 | Free | 8.55 | 3.14 | 0.36725 | 2 | Pass | 8,55 | ເຄື່ອງສົ່ງໃໝ່ PP-NT
8 | Free | 8.58 | 3.12 | 0.36364 | 2 | Pass | 8,58 | ເຄື່ອງສົ່ງໃໝ່ PP-NT
9 | Free | 8.55 | 3.28 | 0.38363 | 2 | Pass | 8,55
10 | Free | 8.58 | 2.97 | 0.34615 | 2 | Pass | 8,58
11 | Free | 8.55 | 3.06 | 0.35789 | 2 | Pass | 8,55
12 | Free | 8.58 | 3.08 | 0.35897 | 2 | Pass | 8,58
13 | PDH |  |  |  | 2 | Pass | PDH | PP-PakOu
14 | Free | 8.56 | 2.92 | 0.34112 | 2 | Pass | 8,56 | Khokwa-Airport
15 | Free | 8.57 | 2.93 | 0.34189 | 2 | Pass | 8,57
16 | Free | 8.57 | 2.93 | 0.34189 | 2 | Fail | 8,58
17 | Free | 8.58 | 3.16 | 0.3683 | 2 | Pass | 8,58
18 | Free | 8.58 | 3.15 | 0.36713 | 2 | Pass | 8,58
19 | Free | 8.58 | 3.06 | 0.35664 | 2 | Pass | 8,58
20 | Internet Hotspot |  |  |  | 2 | Pass | Media | PP-Souphanouvong
21 | Swich |  |  |  | 2 | Pass | Swich | PP-KhokWa
22 | Swich |  |  |  | 2 | Pass | Swich | PP-KhokWa
23 | Free | 2.84 | 5.29 | 1.8627 | 2 | Fail | PDH Phonsaat
24 | Free | 2.84 | 1.09 | 0.3838 | 2 | Fail | PDH Phonsaat
No.IV Mode: 24 Core From "LPB"Phonpheng to "LPB"Khokwa.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 2 |  | PDH | PP-Khokwa
2 | PDH |  |  |  | 2 |  | PDH | PP-Khokwa
3 | STM-16 |  |  |  | 2 |  | STM-16 | PP-Namthouam
4 | STM-16 |  |  |  | 2 |  | STM-16 | PP-Namthouam
5 | Free | 8.59 | 3.55 | 0.41327 | 2 | Pass | 8.59
6 | PDH FE |  |  |  | 2 |  | PDH Souphanouvong | PP-Souphanouvong
7 | Free | 8.59 | 3.55 | 0.41327 | 2 | Pass | 8,55
8 | Free | 8.58 | 3.56 | 0.41492 | 2 | Pass | 8,58
9 | Free | 8.59 | 3.45 | 0.40163 | 2 | Pass | 8,55
10 | Free | 8.56 | 3.46 | 0.40421 | 2 | Pass | 8,58
11 | Free | 8.58 | 3.54 | 0.41259 | 2 | Pass | 8,55
12 | Free | 8.54 | 3.35 | 0.39227 | 2 | Pass | 8,58
13 | PDH FE |  |  |  | 2 |  | PDH FE | PP-PakOu
14 | Free | 8.54 | 3.35 | 0.39227 | 2 | Pass | 8.54
15 | Free | 8.15 | 3.35 | 0.41104 | 2 | Pass | 8.15
16 | Free | 8.15 | 3.65 | 0.44785 | 2 | Pass | 8.15
17 | Free | 8.54 | 3.54 | 0.41452 | 2 | Pass | 8.54
18 | Free | 8.58 | 4.03 | 0.4697 | 2 | Pass | 8.58
19 | Free | 8.59 | 4.04 | 0.47031 | 2 | Pass | 8.59
20 | Media Hotspot |  |  |  | 2 | Pass | Media Hotspot | PP-Souphanouvong
21 | Swich |  |  |  | 2 | Pass | Swich | PP-Khokwa
22 | Swich |  |  |  | 2 | Pass | Swich | PP-Khokwa
23 | PDH |  |  |  | 2 | Pass | 2,84 | BTS Phonsaat
24 | PDH |  |  |  | 2 | Pass | 2,84 | BTS Phonsaat
No.X Mode: 18 Core From "LPB"Khokwa"LPB"Phonpheng .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass | STM-1 | PP-Khokwa
2 | STM-1 |  |  |  |  | Pass | STM-1 | PP-Khokwa
3 | Free | 8,47 | 3,99 |  |  | Pass | 8,47
4 | Free | 8,45 | 4,20 |  |  | Pass | 8,45
5 | PDH |  |  |  |  | Pass | PDH | BTS Souphanouvong
6 | PDH |  |  |  |  | Pass | PDH | 3G Khokwa
7 | [7 empty] | ບໍ່ໄດ້ຕໍ່ອອກ ODF
8 | [7 empty] | ບໍ່ໄດ້ຕໍ່ອອກ ODF
9 | ຕໍ່ຜ່ານ | [6 empty] | ຕໍ່ໃສ່ Core11-PakOu
10 | ຕໍ່ຜ່ານ | [6 empty] | ຕໍ່ໃສ່ Core12-PakOu
11 | [7 empty] | ບໍ່ໄດ້ຕໍ່ອອກ ODF
12 | Free | 8,46 | 3,51 |  |  | Pass | 8,46
13 | Free | 1,22 | 2,32 |  |  | Fail | PDH Phouvao
14 | [5 empty] | Pass |  | ຕໍ່ຜ່ານໄປປາກອູ
15 | [5 empty] | Pass |  | ຕໍ່ຜ່ານໄປປາກອູ
16 | Free | 7.34 | 2.73 |  |  | Fail | Leased-line BOL
17 | PDH |  |  |  |  | Fail | 3,98 | PP-Airport
18 | Free | 8.45 | 3.89 | 0.46036 |  | Pass | 8.45
No.V Mode: 18 Core From "LPB"PakOu to "LPB" Khokwa.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  | 10 | Pass |  | PakOu-Khokwa
2 | STM-1 |  |  |  | 10 | Pass |  | PakOu-Khokwa
3 | Free | 35.12 | 13.61 | 0.38753 | 10 | Pass |  | ເຄື່ອງສົ່ງໃໝ່ PP-NT
4 | Free | 14.39 | 4.98 | 0.34607 | 10 | Fail | Cell 3G Paksuerng
5 | Free | 35.09 | 15.78 | 0.4497 | 10 | Pass |  | Spare PP-NT
6 | Free | 22.93 | 7.91 | 0.34496 | 10 | Fail
7 | Cell2G |  |  |  | 10 | Pass |  | PakOu-Huiymard
8 | Cell2G |  |  |  | 10 | Pass | PDH Paksuerng | PakOu-Huiymard
9 | Free | 14.39 | 5.31 | 0.36901 | 10 | Fail | PDH Souphanouvong
10 | STM-16 |  |  |  | 10 | Pass |  | PP-NT
11 | STM-16 |  |  |  | 10 | Pass |  | PP-NT
12 | Free | 18.44 | 8.7 | 0.4718 | 10 | Fail
13 | Free | 22.46 | 7.94 | 0.35352 | 10 | Fail | 5,48
14 | Free | 22.47 | 8.82 | 0.39252 | 10 | Fail | Media Souphanouvong
15 | Free | 10.33 | 3.78 | 0.36592 | 10 | Fail | 18.29
16 | Free | 10.33 | 3.51 | 0.33979 | 10 | Fail | PDH Outdoor Paksuerng
17 | Free | 30.51 | 10.98 | 0.35988 | 10 | Pass |  | ເຄື່ອງສົ່ງໃໝ່ PP-NT
18 | PDH FE |  |  |  | 10 | Pass |  | PakOu-PP
No.II Mode: 18 Core From "LPB"Khokwa to "LPB"PakOu.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass | STM-1 | Khokwa-PakOu
2 | STM-1 |  |  |  |  | Pass | STM-1 | Khokwa-PakOu
3 | Free | 26.64 | 10.24 | 0.38438 |  | Pass
4 | Cell 3G | [5 empty] | 14,39 | Paksuerng
5 | ຕໍ່ຜ່ານ | [6 empty] | PP-PakOu
6 | ຕໍ່ຜ່ານ | [6 empty] | PP-PakOu
7 | Internet Hotspot | [5 empty] | Cell 2G Huiymard | PP-Souphanouvong
8 | PDH |  |  |  |  | Pass | Cell 2G Huiymard | BTS Paksuerng
9 | PDH FE |  |  |  |  | Pass | 14,39 | PP-Souphanouvong
10 | STM-16 |  |  |  |  | Pass | STM-16 | PP-NT
11 | STM-16 |  |  |  |  | Pass | STM-16 | PP-NT
12 | Spare | [6 empty] | PP-NT
13 | Free | 5.48 | 4.86 | 0.88686 |  | Fail | 22,46
14 | Media |  |  |  |  | Pass | 22,47 | DSLAM Souphanouvong
15 | Free | 18.29 | 9.33 | 0.51011 |  | Fail | 10,33
16 | PDH | [5 empty] | 10,33 | Outdoor Kaset Paksuerng
17 | Free | 30.51 | 9.55 | 0.31301 |  | Pass
18 | PDH FE | [5 empty] | PDH FE | PP-PakOu
No.VI Mode: 18 Core From "LPB"PakOu to "LPB" Namthoum.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 17.09 | 6.18 | 0.36161 | 31 | Fail | PDH NamOu2
2 | Free | 43.59 | 16.93 | 0.38839 | 31 | Fail | PDH Xiengda
3 | PDH |  |  |  | 31 | Pass | PDH NamNga | PakOu-Pakjeak
4 | PDH |  |  |  | 31 | Pass | PDH NamNga | PakOu-Pakjeak
5 | Spare |  |  |  | 31 | Pass | Spare | PP-Namthouam
6 | Free | 49.85 | 18.17 | 0.36449 | 31 | Pass | STM-16 | Spare PP-NT
7 | STM-1 |  |  |  | 31 | Pass | STM-1 | PakOu-NamThouam
8 | Free | 42.64 | 16.36 | 0.38368 | 31 | Fail | Cell 3G Xiengda
9 | Free | 35.87 | 13.27 | 0.36995 | 31 | Fail | Media NamOu 2
10 | Free | 16.18 | 6.38 | 0.39431 | 31 | Fail | PDH DoneNgern
11 | Cell 3G |  |  |  | 31 | Pass | 33,95 | PakOu-NamOu1
12 | Cell 2G |  |  |  | 31 | Pass | 33,95 | PakOu-NamOu2
13 | STM-1 |  |  |  | 31 | Pass | STM-1 | PakOu-Namthouam
14 | Free | 5.5 | 2.37 | 0.43091 | 31 | Fail | 12,65
15 | Free | 48.18 | 17.51 | 0.36343 | 31 | Pass | Cell 2G Xiengda-Thaboo | Spare PP-NT
16 | STM-16 |  |  |  | 31 | Pass | STM-16 | PP-Namthouam
17 | Free | 38.41 | 14.61 | 0.38037 | 31 | Fail | 44,99
18 | Free | 5.54 | 2.18 | 0.3935 | 31 | Fail | Cell 2G Xiengda-Thaboo
No.VII Mode: 18 Core From "LPB"Namthouam to "LPB" PakOu.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 31 | Pass | 17,09 | BTS NamOu2
2 | PDH |  |  |  | 31 | Pass | 43,59 | Xiengda
3 | PDH |  |  |  | 31 | Pass | PDH PakJeak | BTS NamNga
4 | PDH |  |  |  | 31 | Pass | PDH PakJeak | BTS NamNga
5 | Spare |  |  |  | 31 | Pass | Spare | NT-PP
6 | STM-16 |  |  |  | 31 | Pass | STM-16 | NT-PP
7 | STM-1 |  |  |  | 31 | Pass | STM-16 | NT-PakOu
8 | Cell 3G |  |  |  | 31 | Pass | 42,64 | Xiengda
9 | Media |  |  |  | 31 | Pass | 35,87 | DSLAM NamOu2
10 | PDH |  |  |  | 31 | Pass | 16,18 | BTS Donnguen
11 | Free | 33.95 | 13.6 | 0.40059 | 31 | Fail | Cell 3G NamOu1
12 | Free | 33.95 | 13.01 | 0.38321 | 31 | Fail | Cell 2G NamOu1
13 | STM-1 |  |  |  | 31 | Pass | STM-1 | NT-PakOu
14 | Free | 12.65 | 4.92 | 0.38893 | 31 | Fail | 5,50
15 | Cell 2G |  |  |  | 31 | Pass | 48,18 | Xiengda-ThaBoo
16 | STM-16 |  |  |  | 31 | Pass | STM-16 | NT-PP
17 | Free | 44.99 | 16.89 | 0.37542 | 31 | Fail | 38,41
18 | Cell 2G |  |  |  | 31 | Pass | 5,54 | Xiengda-ThaBoo
No.VIII Mode: 18 Core From "LPB"NamThouam to "LPB" Songja.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G | [5 empty] | 19,63 | NT-Nammong
2 | Free | 39.48 | 16.07 | 0.40704 |  | Pass | 39,48
3 | Free | 26.36 | 18.02 | 0.68361 |  | Fail | 19.63
4 | Free | 39,52 | 4.9 | #VALUE! |  | Fail | 25,09
5 | Free | 14.41 | 4.74 | 0.32894 |  | Fail | 25,09
6 | Free | 14.41 | 4.7 | 0.32616 |  | Fail | 25,09
7 | Free | 23.44 | 8.23 | 0.35111 |  | Fail | 16,05
8 | Free | 39.47 | 15.2 | 0.3851 |  | Pass | 39,48 | ເຄື່ອງສົ່ງໃໝ່
9 | Free | 39.47 | 15.2 | 0.3851 |  | Fail | 39,48 | ແທກບໍ່ອອກ
10 | Free | 39.49 | 14.86 | 0.3763 |  | Pass | 39,58 | ເຄື່ອງສົ່ງໃໝ່
11 | Free | 35.27 | 16.58 | 0.47009 |  | Fail | ຕໍ່ຜ່ານ
12 | Free | 39.48 | 16.02 | 0.40578 |  | Pass | 39,48
13 | PDH |  |  |  |  | Pass | PDH | BTS Songja
14 | STM-16 |  |  |  |  | Pass | STM-16 | NT-ODX
15 | PDH |  |  |  |  | Pass | PDH | BTS Songja
16 | STM-16 |  |  |  |  | Pass | STM-16 | NT-ODX
17 | Cell 3G |  |  |  |  | Pass | Repaetor | Pakbak-Pakmong
18 | Media |  |  |  |  | Pass | 12,60 | DSLAM Pakmong
No.IX Mode: 18 Core From "LPB"Songja "LPB" Namthouam
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 19.63 | 8.79 | 0.44778 | 37 | Fail | Cell 2G Nammong
2 | Free | 39.48 | 14.87 | 0.37665 | 37 | Pass | 39,48
3 | Free | 19.63 | 11.06 | 0.56342 | 37 | Fail | 26,36
4 | Free | 25.09 | 10.97 | 0.43723 | 37 | Fail | 14,14
5 | Free | 25.09 | 12.75 | 0.50817 | 37 | Fail | 14,14
6 | Free | 25.08 | 11.08 | 0.44179 | 37 | Fail | 14,14
7 | Free | 16.05 | 8.05 | 0.50156 | 37 | Fail | 23,44
8 | Free | 39,48 | 14.87 | 0.38 | 37 | Pass | 39,48 | ຕໍ່ຜ່ານ
9 | Free | 39.48 | 16.24 | 0.41135 | 37 | Pass | 39,48
10 | Free | 39.49 | 15.19 | 0.38465 | 37 | Pass | 39,48
11 |  |  |  |  | 37 |  | 35,21 | ຕໍ່ຜ່ານ
12 | Free | 39.49 | 15.19 | 0.38465 | 37 | Pass | 39,48 | ແທກບໍ່ອອກ
13 | PDH |  |  |  | 37 | Pass | PDH | BTS SongJa
14 | STM-16 |  |  |  | 37 | Pass | STM-16 | Namthouam-ODX
15 | STM-16 |  |  |  | 37 | Pass | STM-16 | Namthouam-ODX
16 | PDH |  |  |  | 37 | Pass | PDH | BTS SongJa
17 | Repeator |  |  |  | 37 | Pass | Cell 3G Pakbak-Pakmong | KaJet
18 | Free | 12.6 | 5.74 | 0.45556 | 37 | Fail | Media Pakmong
No.X Mode: 18 Core From "LPB"Songja "ODX" Oudomxay.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 13.85 | 5.68 | 0.41011 |  | Fail
2 | STM-64 | [6 empty] | NT-ODX
3 | Free | 13.85 | 5.46 | 0.39422 |  | Fail
4 | Free | 13.85 | 5.54 | 0.4 |  | Fail
5 | STM-64 | [6 empty] | NT-ODX
6 | Free | 13.85 | 5.02 | 0.36245 |  | Fail
7 | Free | 14.56 | 5.83 | 0.40041 |  | Fail
8 | Free | 6.32 | 3.08 | 0.48734 |  | Fail
9 | Free | 6.32 | 2.81 | 0.44462 |  | Fail
10 | Free | 14.65 | 6.57 | 0.44846 |  | Fail
11 | Free | 40 | 15.62 | 0.3905 |  | Pass
12 | Free | 39.47 | 15.91 | 0.40309 |  | Fail
13 | Free | 14.66 | 5.79 | 0.39495 |  | Fail
14 | Free | 3.88 | 1.39 | 0.35825 |  | Fail
15 | Free | 14.66 | 6.9 | 0.47067 |  | Fail
16 | Free | 14.65 | 5.9 | 0.40273 |  | Fail
17 | Repeator | [6 empty] | Pungving
18 | Free | 13.85 | 5.83 | 0.42094 |  | Fail
No.XI Mode: 18 Core From "LPB"Namthouam "LPB" Nambark and Pakmong
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 HW |  |  |  | 11 | Pass |  | NT-PP
2 | STM-64 HW |  |  |  | 11 | Pass |  | NT-PP
3 | STM-64 HW |  |  |  | 11 | Pass |  | NT-ODX
4 | Free | 22.75 | 8.47 | 0.37231 | 11 | Pass |  | ເຄື່ອງສົ່ງໃໝ່
5 | STM-64 HW |  |  |  | 11 | Pass |  | NT-ODX
6 | Free | 2.52 | 1.31 | 0.51984 | 11 | Fail
7 | Cell 2G |  |  |  | 11 | Pass |  | Xiengda-Thaboo
8 | Cell 2G |  |  |  | 11 | Pass |  | Xiengda-Thaboo
9 | PDH |  |  |  | 11 | Pass |  | BTS Pakmong
10 | Free | 3.47 | 1.19 | 0.34294 | 11 | Fail
11 | Free | 3.47 | 1.73 | 0.49856 | 11 | Fail
12 | PDH |  |  |  | 11 | Pass |  | BTS Pakmong
13 | STM-4 |  |  |  | 11 | Pass |  | NT-M.Ngoy
14 | STM-4 |  |  |  | 11 | Pass |  | NT-M.Ngoy
15 | Cell 3G |  |  |  | 11 | Pass |  | Pakbak-Pakmong
16 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
17 | Media |  |  |  | 11 | Pass |  | DSLAM Nambark
18 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
No.XIII Mode: 18 Core From "LPB" Nambark to "LPB" Namthouam.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-4 |  |  |  | 11 | Pass |  | NT-M. Ngoy
2 | Cell 3G |  |  |  | 11 | Pass |  | M.Ngoy-Nambark
3 | Media |  |  |  | 11 | Pass |  | Internet Nambark
4 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
5 | Free | 19.28 | 6.95 | 0.36048 | 11 | Fail
6 | Free | 22.75 | 8.39 | 0.36879 | 11 | Pass |  | ເຄື່ອງສົ່ງໃໝ່
7 | PDH |  |  |  | 11 | Pass |  | BTS Nambark
8 | Cell 3G |  |  |  | 11 | Pass |  | M.Ngoy-Pakmong
No.XIV Mode: 18 Core From "LPB" Nambark to "LPB" M. Ngoy.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-4 |  |  |  | 8 | Pass | PDH B.Lee | NT-M. Ngoy
2 | Cell 3G |  |  |  | 8 | Pass | 14,82 | M.Ngoy-Nambark
3 | Cell 3G |  |  |  | 8 | Pass | PDH B.Lee | M.Ngoy-Pakmong
4 | Free | 7.64 | 4.56 | 0.59686 | 8 | Fail | Cell 3G Pakmong
5 | Free | 17.854 | 7.34 | 0.41111 | 8 | Fail | 3G Nambark | ເຄື່ຶອງສົ່ງໃໝ່
6 | Free | 7.7 | 2.82 | 0.36623 | 8 | Fail | STM-4
7 | STM-4 |  |  |  | 8 | Pass | 3G Nambark
8 | Cell 3G |  |  |  | 8 | Pass | STM-4 | M.Ngoy-Nambark
;l hy
No.XV Mode: 18 Core From "LPB"M.Ngoy to "LPB" M. Nambark.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 8 | Pass | STM-4 | BTS B. Lee
2 | Free | 14.82 | 5.65 | 0.38124 | 8 | Fail | Cell 3G Nambark
3 | PDH |  |  |  | 8 | Pass | 3G Pakmong | BTS B. Lee
4 | Cell 3G |  |  |  | 8 | Pass | 7,64 | Pakmong
5 | Cell 3G |  |  |  | 8 | Pass | 2,79 | Nambark
6 | STM-4 |  |  |  | 8 | Pass | 2,79 | M.Ngoy-Namthouam
7 | Cell 3G |  |  |  | 8 | Pass | STM-4 | Nambark
8 | STM-4 |  |  |  | 8 | Pass | 3G Nambark | M.Ngoy-Namthouam
No.XVI Mode: 18 Core From "LPB"M.Ngoy to "LPB" M. Viengkham.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G |  |  |  | 49 | Pass |  | Nongkhiew-pakbak
2 | Cell 2G |  |  |  | 49 | Pass |  | Nongkhiew-pakbak
3 | Media |  |  |  | 49 | Pass |  | Leased line BCEL
4 | Free | 13.65 | 4.83 | 0.35385 | 49 | Fail
5 | STM-4 |  |  |  | 49 | Pass |  | M.ngoy-M.Viengkham
6 | Free | 53.33 | 17.08 | 0.32027 | 49 | Pass |  | ເຄື່ອງສົ່ງໃໝ່
7 | STM-4 |  |  |  | 49 | Pass |  | M.ngoy-M.Viengkham
8 | PDH |  |  |  | 49 | Pass |  | BTS Phoutidphuerng
9 | PDH |  |  |  | 49 | Pass |  | BTS Phoutidphuerng
10 | Media |  |  |  | 49 | Pass |  | DSLAM Nongkheiw
11 | Cell 3G |  |  |  | 49 | Pass |  | Pakbak-Nongkheiw
12 | Cell 3G |  |  |  | 49 | Pass |  | Pakbak-Nongkheiw
13 | Free | 24.53 | 8.46 | 0.34488 | 49 | Fail
14 | PDH |  |  |  | 49 | Pass |  | BTS Nongkheiw
15 | Free | 4.27 | 1.44 | 0.33724 | 49 | Fail
16 | Repeator |  |  |  | 49 | Pass |  | NongEain
17 | PDH |  |  |  | 49 | Pass |  | BTS Nongkheiw
18 | Free | 4.27 | 1.48 | 0.3466 | 49 | Fail
No.XVII Mode: 18 Core From "LPB"M. Viengkham to "LPB" M. Viengthong.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Unitel |  |  |  | 80 |  |  | Unitel VK-VT
2 | Unitel |  |  |  | 80 |  |  | Unitel VK-VT
3 | Free | 14.29 | 6.51 | 0.45556 | 80 | Fail
4 | PDH |  |  |  | 80 | Pass |  | Phousnam
5 | Free | 8.16 | 3.07 | 0.37623 | 80 | Fail
6 | STM-4 |  |  |  | 80 | Pass |  | Viengkham-viengthong
7 | Cell 2G |  |  |  | 80 |  |  | Viengkham-Sobhuerng
8 | PDH |  |  |  | 80 | Pass |  | Phousnam
9 | Free | 8.2 | 3.1 | 0.37805 | 80 | Fail
10 |  |  |  |  | 80 |  |  | ແທກບໍ່ອອກ
11 | Free | 8.26 | 3.41 | 0.41283 | 80 | Fail
12 | Free | 20.75 | 10.6 | 0.51084 | 80 | Fail
13 | PDH |  |  |  | 80 |  |  | BTS Huiychorc
14 | Free | 18.37 | 6.78 | 0.36908 | 80 | Fail
15 | Free | 8.66 | 3.25 | 0.37529 | 80 | Fail
16 | PDH |  |  |  | 80 |  |  | BTS Huiychorc
17 | Free | 41.99 | 16.86 | 0.40152 | 80 | Fail
18 | STM-4 |  |  |  | 80 | Pass |  | Viengkham-viengthong
No.XVIII Mode: 18 Core From "LPB"XiengNguen "LPB" Phonpheng.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free |  |  |  | 12 | Fail | PDH Nounsavath | ແທກບໍ່ອອກ
2 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Phoukhoun
3 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Phoukhoun
4 | STM-1 |  |  |  | 12 | Pass | STM-1 | xiengNguen-PP
5 | STM-1 |  |  |  | 12 | Pass | STM-1 | xiengNguen-PP
6 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Xayya
7 | Free | 11.86 | 4.56 | 0.38449 | 12 | Fail | PDH
8 | Free | 18.06 | 6.18 | 0.34219 | 12 | Fail | PDH
9 | Free | 18.06 | 6.16 | 0.34109 | 12 | Fail | PDH
10 | Media |  |  |  | 12 | Pass | Media | DSLAM XiengNguen
11 | Media |  |  |  | 12 | Pass | Media | DSLAM XiengNguen
12 | Free | 16.51 | 5.75 | 0.34827 | 12 | Fail | PDH Km-10
13 | Free | 15.07 | 5.12 | 0.33975 | 12 | Fail | 5.05
14 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-Xayya
15 | PDH |  |  |  | 12 | Pass | PDH | PP-Kiewkacham
16 | PDH |  |  |  | 12 | Pass | PDH | PP-Kiewkacham
17 | Free | 21.04 | 7.23 | 0.34363 | 12 | Fail | Media APB
18 | Free | 21.03 | 7.24 | 0.34427 | 12 | Fail | Media APB
No.XIX Mode: 24 Core From "LPB"XiengNguen "LPB" Phonpheng.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-B.Dan
2 | Free | 23.79 | 8.68 | 0.36486 | 12 | Pass | 23.79
3 | Free | 23.79 | 9.35 | 0.39302 | 12 | Pass | 23.79
4 | STM-64 |  |  |  | 12 | Pass | STM-64 | PP-B.Dan
5 | Free | 20.4 | 9.57 | 0.46912 | 12 | Fail | EDL Km-01
6 | PDH |  |  |  | 12 | Pass | PDH | PP-XiengNguen
7 | Spare | 23.97 |  |  | 12 | Pass | 23.97 | PP-kiewkacham
8 | Spare | 23.97 |  |  | 12 | Pass | 23.97 | PP-kiewkacham
9 | Free | 23.97 | 8.53 | 0.35586 | 12 | Pass | 23.97
10 | Free | 23.97 | 8.65 | 0.36087 | 12 | Pass | 23.97
11 | Free | 23.64 | 9.06 | 0.38325 | 12 | Pass | 23.64
12 | Free | 23.76 | 8.71 | 0.36658 | 12 | Pass | 23.76
13 | Free | 20.4 | 7.87 | 0.38578 | 12 | Fail | 4,35
14 | Free | 23.76 | 10.1 | 0.42508 | 12 | Pass | 23.76
15 | Free | 23.76 | 9.46 | 0.39815 | 12 | Pass | 23.76
16 | Free | 23.76 | 9.34 | 0.3931 | 12 | Pass | 23.76
17 | Free | 23.76 | 8.81 | 0.37079 | 12 | Pass | 23.76
18 | Free | 23.75 | 9.03 | 0.38021 | 12 | Pass | 23.75
19 | Free | 14.83 | 5.64 | 0.38031 | 12 | Fail | PDH
20 | Free | 14.82 | 5.28 | 0.35628 | 12 | Fail | PDH
21 | Free | 7.56 | 2.7 | 0.35714 | 12 | Fail | STM 64 PP-NT
22 | Free |  |  |  | 12 |  | STM 64 PP-NT | ແທກບໍ່ອອກ
23 | Free | 9.11 | 3.38 | 0.37102 | 12 | Fail | 7,61
24 | Free | 16.34 | 6.65 | 0.40698 | 12 | Fail | 7,61
No.XX Mode: 18 Core From "LPB"XiengNguen "LPB" Kiewkacham.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM -64 |  |  |  | 44 | Pass | STM-64 | PP-Phoukhoun
2 | Free | 49.55 | 18.64 | 0.37619 | 44 | Pass | 49.55
3 | Spare | 49.56 | 18.64 | 0.37611 | 44 | Pass | 49.56 | PP-Phoukhoun
4 | Spare |  |  |  | 44 | Pass | 49.56 | PP-Phoukhoun
5 | Free | 27.63 | 10.27 | 0.3717 | 44 | Fail | Repeator Namming
6 | Free | 27.37 | 10.82 | 0.39532 | 44 | Fail | Repeator Namming
7 | PDH |  |  |  | 44 | Pass | 43.22 | BTS Namkhan 3
8 | PDH |  |  |  | 44 | Pass | 17.47 | BTS Namkhan 4
9 | Cell 3G |  |  |  | 44 | Pass | 11.56 | Namkhan3
10 | Free | 37.96 | 15.22 | 0.40095 | 44 | Pass | 11.56
11 | Free | 37.92 | 15.87 | 0.41851 | 44 | Fail | 11.56
12 | Free | 37.98 | 15.14 | 0.39863 | 44 | Fail | 11.56
13 | PDH |  |  |  | 44 | Pass | PDH | PP-Keiwkacham
14 | PDH |  |  |  | 44 | Pass | PDH | PP-Keiwkacham
15 | STM -64 |  |  |  | 44 | Pass | STM-64 | PP-Phoukhoun
16 | Free | 2.17 | 1.03 | 0.47465 | 44 | Fail | 45.77
17 | Free | 49.78 | 19.34 | 0.38851 | 44 | Pass | 49.78
18 | Free | 49.79 | 19.35 | 0.38863 | 44 | Pass | 49.78
No.XXI Mode: 18 Core From "LPB"Keiwkacham "LPB" XiengNguen.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 44 | Pass | STM-64 | PP-Phoukhoun
2 | Free | 49.55 | 21.45 | 0.4329 | 44 | Pass | 49.55
3 | Free | 49.56 | 22.54 | 0.4548 | 44 | Pass | 49.56
4 | Free | 49.34 | 21.65 | 0.43879 | 44 | Pass | 49.56
5 | Repeator | 23.13 | 9.09 | 0.393 | 44 | Pass | 27.63 | Keiwkacham-Namming
6 | Repeator | 23.12 | 11.41 | 0.49351 | 44 | Pass | 27.63 | Keiwkacham-Namming
7 | Free | 43.22 | 18.66 | 0.43174 | 44 | Fail | PDH Namkhan3
8 | Free | 17.47 | 7.41 | 0.42416 | 44 | Fail | PDH Namkhan3
9 | Free | 11.56 | 4.47 | 0.38668 | 44 | Fail | Cell 3G Namkhan3
10 | Free | 11.57 | 4.7 | 0.40622 | 44 | Fail | 37.96
11 | Free | 11.57 | 4.5 | 0.38894 | 44 | Fail | 37.96
12 | Free | 11.57 | 4.54 | 0.39239 | 44 | Fail | 37.96
13 | PDH |  |  |  | 44 | Pass | PDH | BTS keiwkacham
14 | PDH |  |  |  | 44 | Pass | PDH | BTS keiwkacham
15 | STM-64 |  |  |  | 44 | Pass | STM-64 | PP-Phoukhoun
16 | Free | 45.77 | 17.78 | 0.38846 | 44 | Fail | 2,17
17 | Free | 49.78 | 16.69 | 0.33528 | 44 | Fail | 49.78
18 | Free | 49.78 | 14.94 | 0.30012 | 44 | Fail | 49.78
No.XXII Mode: 18 Core From "LPB"Keiwkacham "LPB" Phoukoun.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 41 | Pass | STM-64 | PP-Phoukhoun
2 | STM-64 |  |  |  | 41 | Pass | STM-64 | PP-Phoukhoun
3 | Free | 19.23 | 7.28 | 0.37858 | 41 | Fail | 8,66
4 | Free | 19.23 | 7.28 | 0.37858 | 41 | Fail | 29,73
5 | Free | 48.93 | 17.06 | 0.34866 | 41 | Pass | 48.86
6 | Free | 48.94 | 17.59 | 0.35942 | 41 | Pass | 48.86
7 | Free | 18.28 | 7.12 | 0.3895 | 41 | Fail | 30.63
8 | Free | 18.28 | 8.46 | 0.4628 | 41 | Fail | 30.63
9 | Free | 18.28 | 7.39 | 0.40427 | 41 | Fail | 30.63
10 | Free | 18.28 | 6.75 | 0.36926 | 41 | Fail | PDH
11 | Free | 18.28 | 7.13 | 0.39004 | 41 | Fail | 30.63
12 | Free | 18.29 | 7.14 | 0.39038 | 41 | Fail | PDH
13 | Free | 48.86 | 18.81 | 0.38498 | 41 | Pass | 48.86
14 | Free |  |  |  | 41 |  | 48.86 | ແທກບໍ່ອອກ
15 | Free | 48.93 | 17.65 | 0.36072 | 41 | Pass | 48.86
16 | Free | 17.24 | 6.45 | 0.37413 | 41 | Fail | 17,19
17 | Repeator |  |  |  | 41 | Pass | 17,66 | Kiewkacham-NongOun
18 | Free | 21.51 | 9.36 | 0.43515 | 41 | Fail | 11,79
No.XXIII Mode: 18 Core From "LPB"PhouKhoun "LPB"Keiwkacham .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-64 |  |  |  | 41 | Pass | STM-64 | Phoukhoun-PP
2 | STM-64 |  |  |  | 41 | Pass | STM-64 | Phoukhoun-PP
3 | Free | 8.66 | 4.84 | 0.55889 | 41 | Fail | 19,23
4 | Free | 29.73 | 11.71 | 0.39388 | 41 | Fail | 19,23
5 | Free | 48.86 | 17.5 | 0.35817 | 41 | Pass | 48,68
6 | Free | 48.87 | 17.2 | 0.35195 | 41 | Pass | 48,68
7 | Free | 9.7 | 3.73 | 0.38454 | 41 | Fail | 18.22
8 | Free | 30.63 | 12.84 | 0.4192 | 41 | Fail | 18.22
9 | Free | 30.63 | 14.91 | 0.48678 | 41 | Fail | 18.22
10 | PDH |  |  |  | 41 | Pass | 18.22 | BTS Phakiengnoy
11 | Free | 30.64 | 12.47 | 0.40698 | 41 | Fail | 18.22
12 | PDH |  |  |  | 41 | Pass | 18.22 | BTS Phakiengnoy
13 | Free | 48.86 | 18.81 | 0.38498 | 41 | Pass | 48.86
14 | Free | 48.87 | 18.82 | 0.3851 | 41 | Pass | 48.86
15 | Free | 48.86 | 18.73 | 0.38334 | 41 | Pass | 48.86
16 | Free | 17.19 | 8.3 | 0.48284 | 41 | Fail | 17,24
17 | Free | 17.66 | 8.11 | 0.45923 | 41 | Fail | Repeator NongOun
18 | Free | 11.79 | 4.66 | 0.39525 | 41 | Fail | 21,51
No.XXIV Mode: 18 Core From "LPB"Phoukoun "Kasi" Kasi
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | PK-Kasi
2 | Free | 4.76 | 1.65 | 0.34 |  | Fail
3 | Free | 42.13 | 16.16 | 0.38 |  | Pass
4 | STM-1 |  |  |  |  | Pass |  | PK-Kasi
5 | STM-64 |  |  |  |  | Pass |  | PK-Kasi
6 | STM-64 |  |  |  |  | Pass |  | PK-Kasi
7 | Free | 13.95 | 5.34 | 0.3828 |  | Fail
8 | Free | 37.64 | 14.91 | 0.39612 |  | Fail
9 | Free | 23.28 | 9.08 | 0.39003 |  | Fail
10 | Free | 23.05 | 9.37 | 0.40651 |  | Fail
11 | Free | 13.95 | 5.71 | 0.40932 |  | Fail
12 | Free | 13.95 | 5.46 | 0.3914 |  | Fail
13 | Free | 10.86 | 4.41 | 0.40608 |  | Fail
14 | Free | 6.44 | 2.72 | 0.42236 |  | Fail
15 | Free | 13.21 | 6.72 | 0.50871 |  | Fail
16 | Free | 13.21 | 5.09 | 0.38531 |  | Fail
17 | Free | 13.22 | 6.23 | 0.47126 |  | Fail
18 | Free | 13.21 | 6.01 | 0.45496
No.XXV Mode: 12 Core From "LPB"Phoukhoun "LPB" XiengKhouang.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-16 |  |  |  |  | Pass |  | Phoukoun-Xiengkhouang
2 | STM-16 |  |  |  |  | Pass |  | Phoukoun-Xiengkhouang
3 | PDH |  |  |  |  | Pass |  | BTS Phousong
4 | Free | 6.51 | 3.32 | 0.50998 |  | Fail
5 | PDH |  |  |  |  | Pass |  | BTS Phousong
6 | Free | 45.37 | 17.77 | 0.39167 |  | Fail
7 | Free | 42.56 | 16.97 | 0.39873 |  | Fail
8 | Free | 46.01 | 18.17 | 0.39491 |  | Fail
9 | Free | 46.81 | 18.09 | 0.38646 |  | Fail
10 | Free | 43.09 | 17.53 | 0.40682 |  | Fail
11 | PDH |  |  |  |  | Pass |  | PK-NamNguerm 5
12 | PDH |  |  |  |  | Pass |  | PK-NamNguerm 5
13
No.XXVI Mode: 18 Core From "LPB"XiengNguen "LPB" B Dan.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 23.06 | 9.07 | 0.39332 | 52 | Fail | 2.43
2 | Free | 24.79 | 10.4 | 0.41952 | 52 | Pass | 10.53
3 | STM-64 |  |  |  | 52 | Pass | STM-64 | PP-B.Dan
4 | STM-64 |  |  |  | 52 | Pass | STM-64 | PP-B.Dan
5 | Free | 23.6 | 9.6 | 0.40678 | 52 | Fail | PDH Silalek
6 | Free | 24.78 | 10.9 | 0.43987 | 52 | Pass | STM-64 HW
7 | PDH |  |  |  | 52 | Pass | STM-64 HW | BTS Slalek
8 | Free | 12.87 | 5.04 | 0.39161 | 52 | Fail | 10.53
9 | Free | 12.88 | 5.05 | 0.39208 | 52 | Fail | STM-1
10 | Free | 23.6 | 9.71 | 0.41144 | 52 | Fail | 12,26
11 | STM-1 |  |  |  | 52 | Pass | STM-1 | XiengNguen-M.Nan
12 | Free | 32.45 | 14.06 | 0.43328 | 52 | Pass | PDH Silalek
13 | Free |  |  |  | 52 |  | 10.54 | ແທກບໍ່ອອກ
14 | PDH |  |  |  | 52 | Pass | 10.53 | BTS Silalek
15 | STM-64 |  |  |  | 52 | Pass | 10.53 | PP-Xayya
16 | Media |  |  |  | 52 | Pass | 4.76 | Internet Huiykod
17 | STM-64 |  |  |  | 52 | Pass | 34.45 | PP-Xayya
18 | STM-1 |  |  |  | 52 | Pass | 34,32 | PP-M.Nan
No.XXVII Mode: 18 Core From "LPB"B.Dan "LPB"XiengNguen .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 2.43 | 2.1 | 0.8642 | 52 | Fail | 23,06
2 | Free | 10.53 | 5.53 | 0.52517 | 52 | Fail | 24,79
3 | STM-64 |  |  |  | 52 | Pass | SMT-64 | B.Dan-PP
4 | STM-64 |  |  |  | 52 | Pass | SMT-64 | B.Dan-PP
5 | PDH |  |  |  | 52 | Pass | 23,66 | B.Dan-Silalek
6 | STM-64 HW |  |  |  | 52 | Pass | 24,78 | PP-Xayyya
7 | STM-64 HW |  |  |  | 52 | Pass | PDH silalek | PP-Xayyya
8 | Free | 10.53 | 5.87 | 0.55745 | 52 | Fail | 12,87
9 | STM-1 |  |  |  | 52 | Pass | 12,88 | XiengNguen-M.Nan
10 | Free | 12.26 | 6.71 | 0.54731 | 52 | Fail | 23,60
11 | STM-1 |  |  |  | 52 | Pass | SMT-1 | XiengNguen-M.Nan
12 | PDH |  |  |  | 52 | Pass | 32,45 | B.Dan-Silalek
13 | Free | 10.54 | 5.12 | 0.48577 | 52 | Fail | ແທກບໍ່ອອກ
14 | Free | 10.53 | 5.89 | 0.55935 | 52 | Fail | PDH silalek
15 | Free | 10.53 | 8.34 | 0.79202 | 52 | Fail | STM-64
16 | Free | 4.76 | 2.26 | 0.47479 | 52 | Fail | Media
17 | Free | 34.45 | 17.2 | 0.49927 | 52 | Pass | STM-64
18 | Free | 34.32 | 17.87 | 0.52069 | 52 | Pass | STM-1
No.XXVIII Mode: 18 Core From "LPB"B.Dan "LPB"M. Nan .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 6.69 | 2.63 | 0.39312 | 19 | Fail | Cell 2G Nalao
2 | Free | 6.74 | 2.68 | 0.39763 | 19 | Fail | Cell 2G Nalao
3 | Free | 6.71 | 2.69 | 0.40089 | 19 | Fail | 8,22
4 | Free | 6.78 | 2.66 | 0.39233 | 19 | Fail | ຕໍ່ຜ່ານ
5 | Free | 6.71 | 2.65 | 0.39493 | 19 | Fail | 6.74
6 | Free | 6.74 | 2.68 | 0.39763 | 19 | Fail | 8.23
7 | STM-1 |  |  |  | 19 | Pass | STM-1 | XiengNguen-M.Nan
8 | STM-64 HW |  |  |  | 19 | Pass | STM-64 HW | PP-Xayya
9 | STM-1 |  |  |  | 19 | Pass | STM-1 | XiengNguen-M.Nan
10 | STM-64 HW |  |  |  | 19 | Pass | STM-64 HW | PP-Xayya
11 | Free | 2.23 | 1.02 | 0.4574 | 19 | Fail | 8,22
12 | STM-64 |  |  |  | 19 | Pass | STM-64 | B.Dan-Xayya
13 | Free | 4.8 | 2.65 | 0.55208 | 19 | Fail | PDH
14 | PDH |  |  |  | 19 | Pass | PDH | B.Dan-Phousacan
15 | PDH |  |  |  | 19 | Pass | STM-64 | B.Dan-Phousacan
16 | Free | 12.07 | 3.63 | 0.30075 | 19 | Fail | ຕໍ່ຜ່ານ
17 | STM-64 |  |  |  | 19 | Pass | STM-64 | B.Dan-Xayya
18 | Free | 12.07 | 3.87 | 0.32063 | 19 | Fail | Cell 2G Keomany
No.XXIX Mode: 18 Core From "LPB"M.Nan "LPB"B.Dan .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G |  |  |  | 19 | Pass | 6.69 | Nalao
2 | Cell 2G |  |  |  | 19 | Pass | 6.74 | Nalao
3 | Free | 8.22 | 3.31 | 0.40268 | 19 | Fail | 6.72
4 |  |  |  |  | 19 |  | 6.72 | ຕໍ່ຜ່ານ
5 | Free | 8.22 | 3.22 | 0.39173 | 19 | Fail | 6.72
6 | Free | 6.74 | 2.68 | 0.39763 | 19 | Fail | 6.72
7 | STM-1 |  |  |  | 19 | Pass | STM-1 | M.Nan-XiengNguen
8 | STM-64 HW |  |  |  | 19 | Pass | STM-64 Hw | PP-Xayya
9 | STM-1 |  |  |  | 19 | Pass | STM-1 | M.Nan-XiengNguen
10 | STM-64 HW |  |  |  | 19 | Pass | STM-64 Hw | PP-Xayya
11 | Free | 8.22 | 3.29 | 0.40024 | 19 | Fail | 2,23
12 | STM-64 |  |  |  | 19 | Pass | STM-64 | B.Dan-Xayya
13 | PDH |  |  |  | 19 | Pass | 4,80 | M.Nan-Phousacan
14 | PDH |  |  |  | 19 | Pass | PDH | M.Nan-Phousacan
15 | STM-64 |  |  |  | 19 | Pass | STM-64 | B.Dan-Xayya
16 |  |  |  |  | 19 |  | 12,07 | ຕໍ່ຜ່ານ
17 | Media |  |  |  | 19 | Pass | Media | Leased Line LDB M.Nan
18 | Cell 2G |  |  |  | 19 | Pass | 12,07 | Keomany
No.XXX Mode: 18 Core From "LPB"M.Nan "XLY"Sayyabouly .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM-1 |  |  |  |  | Pass |  | M.Nan-Xayya
2 | Free | 8.77 | 2.79 | 0.31813 |  | Pass |  | ThaDuer XYL
3 | STM-1 |  |  |  |  | Pass |  | M.Nan-Xayya
4 | 8,77 | 3.04 |  |  |  | Pass |  | ThaDuer XYL
5 | Free | 8.77 | 3.26 | 0.37172 |  | Pass |  | ThaDuer XYL
6 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
7 | Free | 8.77 | 3.32 | 0.37856 |  | Pass |  | ThaDuer XYL
8 | Free | 8.77 | 3 | 0.34208 |  | Pass |  | ThaDuer XYL
9 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
10 | STM-64 HW |  |  |  |  | Pass |  | PP-Xayya
11 | STM-64 |  |  |  |  | Pass |  | B.Dan-Xayya
12 | [7 empty] | ຕໍ່ຜ່ານ
13 | [7 empty] | ຕໍ່ຜ່ານ
14 | Free | 8.78 | 3.03 | 0.3451 |  | Pass |  | ThaDuer XYL
15 | Free | 8.77 | 3.15 | 0.35918 |  | Pass |  | ThaDuer XYL
16 | Free | 8.77 | 3.21 | 0.36602 |  | Pass |  | ThaDuer XYL
17 | Free | 5.14 | 1.75 | 0.34047 |  | Fail
18 | Free | 5.14 | 1.78 | 0.3463 |  | Fail

## Sheet3
No.XXVIII Mode: 18 Core From "LPB"B.Dan "LPB"M. Nan .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 6.69 | 2.63 | 0.39312 | 19 | Fail
2 | Free | 6.74 | 2.68 | 0.39763 | 19 | Fail
3 | Free | 6.71 | 2.69 | 0.40089 | 19 | Fail
4 | Free | 6.78 | 2.66 | 0.39233 | 19 | Fail
5 | Free | 6.71 | 2.65 | 0.39493 | 19 | Fail
6 | Free | 6.74 | 2.68 | 0.39763 | 19 | Fail
7 | STM-1 |  |  |  | 19 | Pass |  | XiengNguen-M.Nan
8 | STM-64 HW |  |  |  | 19 | Pass |  | PP-Xayya
9 | STM-1 |  |  |  | 19 | Pass |  | XiengNguen-M.Nan
10 | STM-64 HW |  |  |  | 19 | Pass |  | PP-Xayya
11 | Free | 2.23 | 1.02 | 0.4574 | 19 | Fail
12 | STM-64 |  |  |  | 19 | Pass |  | B.Dan-Xayya
13 | Free | 4.8 | 2.65 | 0.55208 | 19 | Fail
14 | PDH |  |  |  | 19 | Pass |  | B.Dan-Phousacan
15 | PDH |  |  |  | 19 | Pass |  | B.Dan-Phousacan
16 | Free | 12.07 | 3.63 | 0.30075 | 19 | Fail
17 | STM-64 |  |  |  | 19 | Pass |  | B.Dan-Xayya
18 | Free | 12.07 | 3.87 | 0.32063 | 19 | Fail

## Sheet2
No.XXIX Mode: 18 Core From "LPB"M.Nan "LPB"B.Dan .
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G |  |  |  | 19 | Pass |  | Nalao
2 | Cell 2G |  |  |  | 19 | Pass |  | Nalao
3 | Free | 8.22 | 3.31 | 0.40268 | 19 | Fail
4 |  |  |  |  | 19 |  |  | ຕໍ່ຜ່ານ
5 | Free | 8.22 | 3.22 | 0.39173 | 19 | Fail
6 | Free | 6.74 | 2.68 | 0.39763 | 19 | Fail
7 | STM-1 |  |  |  | 19 | Pass |  | M.Nan-XiengNguen
8 | STM-64 HW |  |  |  | 19 | Pass |  | PP-Xayya
9 | STM-1 |  |  |  | 19 | Pass |  | M.Nan-XiengNguen
10 | STM-64 HW |  |  |  | 19 | Pass |  | PP-Xayya
11 | Free | 8.22 | 3.29 | 0.40024 | 19 | Fail
12 | STM-64 |  |  |  | 19 | Pass |  | B.Dan-Xayya
13 | PDH |  |  |  | 19 | Pass |  | M.Nan-Phousacan
14 | PDH |  |  |  | 19 | Pass |  | M.Nan-Phousacan
15 | STM-64 |  |  |  | 19 | Pass |  | B.Dan-Xayya
16 |  |  |  |  | 19 |  |  | ຕໍ່ຜ່ານ
17 | Media |  |  |  | 19 | Pass |  | Leased Line LDB M.Nan
18 | Cell 2G |  |  |  | 19 | Pass |  | Keomany

## NT-PakOu
No.VII Mode: 18 Core From "LPB"Namthouam to "LPB" PakOu.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 31 | Pass | 17,09 | BTS NamOu2
2 | PDH |  |  |  | 31 | Pass | 43,59 | Xiengda
3 | PDH |  |  |  | 31 | Pass | PDH PakJeak | BTS NamNga
4 | PDH |  |  |  | 31 | Pass | PDH PakJeak | BTS NamNga
5 | Spare |  |  |  | 31 | Pass | Spare | NT-PP
6 | STM-16 |  |  |  | 31 | Pass | STM-16 | NT-PP
7 | STM-1 |  |  |  | 31 | Pass | STM-16 | NT-PakOu
8 | Cell 3G |  |  |  | 31 | Pass | 42,64 | Xiengda
9 | Media |  |  |  | 31 | Pass | 35,87 | DSLAM NamOu2
10 | PDH |  |  |  | 31 | Pass | 16,18 | BTS Donnguen
11 | Free | 33.95 | 13.6 | 0.40059 | 31 | Fail | Cell 3G NamOu1
12 | Free | 33.95 | 13.01 | 0.38321 | 31 | Fail | Cell 2G NamOu1
13 | STM-1 |  |  |  | 31 | Pass | STM-1 | NT-PakOu
14 | Free | 12.65 | 4.92 | 0.38893 | 31 | Fail | 5,50
15 | Cell 2G |  |  |  | 31 | Pass | 48,18 | Xiengda-ThaBoo
16 | STM-16 |  |  |  | 31 | Pass | STM-16 | NT-PP
17 | Free | 44.99 | 16.89 | 0.37542 | 31 | Fail | 38,41
18 | Cell 2G |  |  |  | 31 | Pass | 5,54 | Xiengda-ThaBoo

## nt-songja
No. Core
No. Core | Traffic (Equipment) | Distand Core(KM) | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell 2G
2 | Free | 39.48 | Pass
3 | Free | 39.52 | Pass
4 | Free | 39.52 | Pass
5 | Free | 39.52 | Pass
6 | Free | 39.52 | Pass
7 | Free | 23.44 | Fail
8 | Free | 39.47 | Pass |  | ເຄື່ອງສົ່ງໃໝ່
9 | Free | 39.47 | Fail
10 | Free | 39.49 | Pass |  | ເຄື່ອງສົ່ງໃໝ່
11 | Free | 35.27 | Fail
12 | Free | 39.48 | Pass
13 | PDH |  | Pass |  | BTS Songja
14 | Free | 39.52 | Pass
15 | PDH |  | Pass |  | BTS Songja
16 | Free | 39.52 | Pass
17 | Cell 3G |  | Pass |  | Pakbak-Pakmong
18 | Media |  | Pass |  | DSLAM Pakmong

## vk-vT
No.XVII Mode: 18 Core From "LPB"M. Viengkham to "LPB" M. Viengthong.
No. Core | Traffic (Equipment) | Distand Core(KM) | Problem Interface (Fault Piont) | Remark
1 | Free | 4,39
2 | Free | 118,06 |  | ຕິດຕັ້ງເຄື່ອງສົ່ງໃໝ່
3 | Free | 14,29
4 | PDH |  |  | Phousnam
5 | Free | 20,77
6 | STM-4 |  |  | Viengkham-viengthong
7 | Free | 63,87
8 | PDH |  |  | Phousnam
9 | Free | 8.2
10 |  |  |  | ແທກບໍ່ອອກ
11 | Free | 40,88
12 | Free | 20.75
13 | PDH |  |  | BTS Huiychorc
14 | Free | 18.37
15 | Free | 34,59
16 | PDH |  |  | BTS Huiychorc
17 | Free | 118,05 |  | ຕິດຕັ້ງເຄື່ອງສົ່ງໃໝ່
18 | STM-4 |  |  | Viengkham-viengthong

## Sheet4
No.IX Mode: 18 Core From "LPB"Namthouam to "LPB" PakOu.
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH |  |  |  | 31 | Pass |  | DSLAM NamOu2
2 | PDH |  |  |  | 31 | Pass |  | Xiengda
3 | PDH |  |  |  | 31 | Pass |  | BTS NamNga
4 | PDH |  |  |  | 31 | Pass |  | BTS NamNga
5 | Spare |  |  |  | 31 | Pass |  | NT-PP
6 | STM-16 |  |  |  | 31 | Pass |  | NT-PP
7 | STM-1 |  |  |  | 31 | Pass |  | NT-PakOu
8 | Cell 3G |  |  |  | 31 | Pass |  | Xiengda
9 | Media |  |  |  | 31 | Pass |  | BTS NamOu2
10 | PDH |  |  |  | 31 | Pass |  | BTS Donnguen
11 | ເຄື່ອງສົົ່ງໃໝ່ |  |  |  | 31 | Pass |  | ເຄື່ອງສົົ່ງໃໝ່
12 | ເຄື່ອງສົົ່ງໃໝ່ |  |  |  | 31 | Fail |  | ເຄື່ອງສົົ່ງໃໝ່
13 | STM-1 |  |  |  | 31 | Pass |  | NT-PakOu
14 | Free | 12,65 | 4,92 | 0,38 | 31 | Fail
15 | Cell 2G |  |  |  | 31 | Pass |  | Xiengda-ThaBoo
16 | STM-16 |  |  |  | 31 | Pass |  | NT-PP
17 | Free | 44,99 | 16,89 | 0,37 | 31 | Fail
18 | Cell 2G |  |  |  | 31 | Pass |  | Xiengda-ThaBoo

## Phoumork
ODF: 1
Station From: To: |  | Phoumork |  |  | TO: |  | Phonepheng | Distance: 2.756 km
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 2.756 |  |  | 1 | Pass
2 | FTTH |  |  |  |  | Pass
3 | PDH | 2.756 |  |  |  | Pass |  | Phoumork - Phonpheng
4 | Free | 2.756 |  |  | 1 | Pass
5 | Free | 2.756 |  |  | 1 | Pass
6 | Free | 2.756 |  |  | 1 | Pass
7 | Free | 2.756 |  |  | 1 | Pass
8 | Free | 2.756 |  |  | 1 | Pass
Update By:
Date:
Station From: To: |  | Phoumork |  |  | TO: |  | BanOu | Distance: km
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Cell@3G tadkuangsi |  |  |  |  | Pass |  | Phoumork - Tadkuangsi
2 | Free |  |  |  |  | Fail
3 | PDH.Aerodev |  |  |  |  | Pass |  | Phoumork - BanOu
4 | PDH.Aerodev |  |  |  |  | Pass |  | Phoumork - BanOu
5 | Free
6 | Free
7 | PDH.Aerodev |  |  |  |  | Pass |  | Phoumork - Houypai
8 | PDH.Aerodev |  |  |  |  | Pass |  | Phoumork - Houypai

## Phonepheng
ODF: 1
Station From: To: |  | Phonepheng |  |  | TO: |  | Phoumork | Distance: 2.756 km
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 2.756 |  |  | 1 | Pass
2 | FTTH |  |  |  |  | Pass
3 | PDH | 2.756 |  |  |  | Pass |  | P.Pheng - Phoumork
4 | Free | 2.756 |  |  | 1 | Pass
5 | Free | 2.756 |  |  | 1 | Pass
6 | Free | 2.756 |  |  | 1 | Pass
7 | Free | 2.756 |  |  | 1 | Pass
8 | Free | 2.756 |  |  | 1 | Pass
Update By:
Date:
Station From: To: |  | Phonepheng |  |  | TO: |  | Phouvao | Distance: km
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 6.4801 | 2.163 | 0.334 | 2 | Fail
2 | Free | 6.9244 | 2.494 | 0.36 | 2 | Fail
3 | Free | 6.6538 | 2.194 | 0.33 | 2 | Fail
4 | Free | 6.6027 | 2.394 | 0.363 | 2 | Fail
5 | Free | 13.6139 | 5.138 | 0.377 | 2 | Pass
6 | PDH.Aerodev |  |  |  |  | Pass |  | Napho - B.Phia
7 | Free | 7.3942 | 2.595 | 0.337 | 2 | Fail
8 | PDH.Aerodev |  |  |  |  | Pass |  | Napho - B.Phia

## B.Phia
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | B.Phia |  |  | TO: |  | Napho
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH.Aerodev | [6 empty] | Napho - Pakseng
2 | PDH.Aerodev | [6 empty] | Napho - Pakseng
3 | Link BackUp | 57.4941 | 24.175 | 0.42 | 7
4 | Link BackUp | 57.4992 | 21.472 | 0.42 | 6
5 | Free | 13.1501 | 4.596 | 0.349 | 3 | Fail
6 | Free | 10.4326 | 9.66 | 0.926 | 2 | Fail
7 | Free | 13.1901 | 4.511 | 0.342 | 3 | Fail
8 | Free | 10.8156 | 6.702 | 0.62 | 2 | Fail
Update By:
Date:
Station From: To: |  | B.Phia |  |  | TO: |  | Paksueng
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 6.4801 | 2.163 | 0.334 | 2 | Fail
2 | Free | 6.9244 | 2.494 | 0.36 | 2 | Fail
3 | Free | 6.6538 | 2.194 | 0.33 | 2 | Fail
4 | Free | 6.6027 | 2.394 | 0.363 | 2 | Fail
5 | Free | 13.6139 | 5.138 | 0.377 | 2 | Pass
6 | PDH.Aerodev |  |  |  |  | Pass |  | Napho - B.Phia
7 | Free | 7.3942 | 2.595 | 0.337 | 2 | Fail
8 | PDH.Aerodev |  |  |  |  | Pass |  | Napho - B.Phia

## Napho
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Napho |  |  | TO: |  | Pakseng
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH.Aerodev | [6 empty] | Napho - Pakseng
2 | PDH.Aerodev | [6 empty] | Napho - Pakseng
3 | Link BackUp | [6 empty] | Pakseng - B.Phia
4 | Free | 19.2975 | 7.035 | 0.365 | 4 | Pass
5 | Free | 19.3077 | 6.529 | 0.338 | 2 | Pass
6 | Link BackUp | [6 empty] | Pakseng - B.Phia
| Rep.Nongfaded | 6.0665 | 2.045 | 0.337 | 2 | Pass
| Rep.VangNguen | 6.0972 | 2.082 | 0.342 | 2 | Fail
Update By:
Date:
Station From: To: |  | Napho |  |  | TO: |  | B.Phia
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH.Aerodev | [6 empty] | Napho - B.Phia
2 | PDH.Aerodev | [6 empty] | Napho - B.Phia
3 | Link BackUp | [6 empty] | Pakseng - B.Phia
4 | Link BackUp | [6 empty] | Pakseng - B.Phia
5 | Free | 24.0108 | 7.914 | 0.33 | 2 | Pass
6 | Free | 13.1033 | 4.371 | 0.334 | 2 | Fail |  | Pakseng - B.Phia
| Free | 24.5112 | 8.312 | 0.339 | 3 | Pass
| Free | 24.501 | 8.094 | 0.33 | 2 | Pass

## Pakseng
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Pakseng |  |  | TO: |  | Napho
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH.Aerodev | [6 empty] | Pakseng - Napho
2 | PDH.Aerodev | [6 empty] | Pakseng - Napho
3 | Link BackUp | 57.4737 | 23.297 | 0.405 | 7 | Pass |  | Pakseng - B.Phia
4 | Free | 19.2975 | 7.01 | 0.363 | 4 | Pass
5 | Free | 19.3077 | 6.517 | 0.338 | 3 | Pass
6 | Link BackUp | 57.893 | 21.716 | 0.378 | 7 | Pass |  | Pakseng - B.Phia
| Free | 6.4495 | 2.366 | 0.367 | 2 | Fail
| Free | 6.7968 | 2.636 | 0.388 | 2 | Fail
Update By:
Date:

## M.Phonxay
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | M.Phonxay |  |  | TO: |  | Paksueng
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free |  |  |  |  | Fail
2 | Free | 9.5083 | 6.186 | 0.651 | 2 | Fail
3 | Free | 31.0031 | 13.681 | 0.441 | 6 | Fail
4 | Free | 29.4798 | 13.23 | 0.449 | 3 | Fail
5 | PDH.Aerodev | [6 empty] | M.PhonXay - Paksueng
6 | PDH.Aerodev | [6 empty] | M.PhonXay - Paksueng
7 | ATM.LDB |  |  |  |  | Pass |  | ຕໍ່ຜ່ານໄປຫາຄໍເຊີ LDB
8 | Free |  |  |  |  | Pass |  | ຕໍ່ຜ່ານໄປຫາຄໍເຊີ LDB
Update By:
Date:

## M.Nan
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | M.Nan |  |  | TO: |  | Phousacan
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Ext.Cell.2G |  |  |  |  | Pass |  | Nalao_Cell_1
2 | Ext.Cell.2G |  |  |  |  | Pass |  | Nalao_Cell_2&3
3 | STM64.Alcatel |  |  |  |  | Pass |  | B.Dan -Xayya
4 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
5 |  | 10.3151 | 4.088 | 0.396 | 3 | Pass
6 |  | 10.2998 | 4.484 | 0.435 | 3 | Pass
7 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
8 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
9 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
10 |  | 10.3151 | 4.088 | 0.373 | 3 | Pass
11 |  | 10.2743 | 4.294 | 0.418 | 3 | Pass
12 | STM64.Alcatel |  |  |  |  | Pass |  | B.Dan -Xayya
13 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan-M.Nan
14 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan-M.Nan
15 |  | 4.795 | 1.779 | 0.373 | 2 | Fail
16 |  | 7.3125 | 2.655 | 0.363 | 2 | Fail
17 | LeaseLine | [6 empty] | LDB
18 | Ext.Cell.2G | [6 empty] | Keomany
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | M.Nan |  |  | TO: |  | Xayya
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 |  | 11.2956 | 4.047 | 0.358 | 3
2 | STM-1 |  |  |  |  | Pass |  | M.Nan - Xayya
3 | STM-1 |  |  |  |  | Pass |  | M.Nan - Xayya
4 |  | 11.556 | 4.15 | 0.359 | 3
5 |  | 32.4773 | 12.167 | 0.375 | 7
6 |  | 11.0198 | 3.639 | 0.33 | 3
7 |  | 11.2803 | 3.744 | 0.332 | 3
8 |  | 11.0198 | 3.547 | 0.332 | 2
9 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
10 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
11 | STM64.Alcatel |  |  |  |  | Pass |  | B.Dan -Xayya
12 |  | 11.0147 | 4.16 | 0.378 | 2
13 | STM64.Alcatel |  |  |  |  | Pass |  | B.Dan -Xayya
14 |  | 40.4282 | 15.231 | 0.337 | 5
15 |  | 40.4231 | 14.757 | 0.365 | 6
16 |  | 11.0147 | 3.813 | 0.346 | 2
17 |  | 5.0146 | 1.387 | 0.277 | 2
18 |  | 5.1576 | 1.914 | 0.371 | 2
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | M.Nan |  |  | TO: |  | Khoktom
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 | Free | 14.1859 | 6.243 | 0.44 | 2 | Pass
2 | Free | 14.1654 | 6.193 | 0.437 | 3 | Pass
3
4
5 | Free | 14.1654 | 4.728 | 0.334 | 3 | Pass
6
7
8
Update By:
Date:

## Phousacan
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phousacan |  |  | TO: |  | B.dan
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM64.Alcatel |  |  |  |  | Pass |  | B.Dan - Xayya
2 | STM64.Alcatel |  |  |  |  | Pass |  | B.Dan - Xayya
3 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
4 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
5 |  | 12.2199 | 5.966 | 0.488 | 8
6 |  | 12.2224 | 4.433 | 0.363 | 8
7 |  | 12.2224 | 6.431 | 0.526 | 8
8 |  | 12.2224 | 6.411 | 0.525 | 11
9 |  | 12.2224 | 6.644 | 0.544 | 9
10 |  | 12.2224 | 5.7 | 0.466 | 11
11 |  | 9.973 | 5.929 | 0.594 | 9
12 |  | 12.2199 | 5.675 | 0.464 | 11
13 |  | 7.4146 | 2.701 | 0.364 | 5
14 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan - Phousacan
15 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan - Phousacan
16 |  | 12.2275 | 5.093 | 0.417 | 11
17 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
18 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phousacan |  |  | TO: |  | M.Nan
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 |  | 8.7525 | 6.271 | 0.717 | 17 | Fail |  | ຮອດຫົວຄໍເຊີແຍກເຂົ້າ Nalao
2 |  | 8.7551 | 3.791 | 0.433 | 12 | Fail |  | ຮອດຫົວຄໍເຊີແຍກເຂົ້າ Nalao
3 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-B.Dan
4 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
5 |  | 10.2973 | 5.935 | 0.576 | 15 | Pass
6 |  | 11.2973 | 4.617 | 0.449 | 11 | Pass
7 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
8 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
9 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
10 |  | 10.2947 | 5.044 | 0.49 | 15 | Pass
11 |  | 10.2947 | 5.191 | 0.504 | 13 | Pass
12 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-B.Dan
13 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan-M.Nan
14 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan-M.Nan
15 |  | 5.5763 | 4.506 | 0.808 | 11
16 |  | 2.8367 | 1.377 | 0.486 | 5
17 |  | 8.5457 | 5.155 | 0.603 | 13
18 |  | 8.5457 | 4.504 | 0.527 | 14
Update By:
Date:

## B.Dan
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | B.Dan |  |  | TO: |  | Silalek
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 |  | 16.9536 | 6.883 | 0.406 | 1 | Pass
2 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-B.Dan
3 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-B.Dan
4 | Free | 14.8089 | 6.045 | 0.408 | 1 | Pass
5 | PDH.Aerodev |  |  |  |  | Pass
6 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
7 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
8 |  | 10.5705 | 5.547 | 0.525 | 3 | Pass
9 | STM-1 |  |  |  |  | Pass |  | sa
10 |  | 10.5705 | 5.984 | 0.566 | 4 | Pass
11 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
12 |  | 10.5705 | 5.668 | 0.536 | 3 | Pass
13 | PDH.Aerodev |  |  |  |  | Pass
14 |  | 10.5756 | 6.181 | 0.584 | 3 | Pass
15 |  | 10.5756 | 7.012 | 0.663 | 4 | Pass
16 |  | 10.5756 | 5.457 | 0.516 | 4 | Pass
17 |  | 10.5756 | 7.802 | 0.738 | 4 | Pass
18 |  | 10.5756 | 5.612 | 0.531 | 4 | Pass
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | B.dan |  |  | TO: |  | Phousacan
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-B.Dan
2 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-B.Dan
3 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
4 | STM64.Huawei |  |  |  |  | Pass |  | Phonepheng-Xayya
5 |  | 12.225 | 4.416 | 0.361 | 3 | Pass
6 |  | 12.2301 | 4.336 | 0.355 | 2 | Pass
7 |  | 12.2301 | 4.65 | 0.38 | 2 | Pass
8 |  | 12.2301 | 4.687 | 0.383 | 2 | Pass
9 |  | 12.225 | 4.44 | 0.363 | 2 | Pass
10 |  | 12.2301 | 4.595 | 0.376 | 2 | Pass
11 |  | 11.3109 | 8.046 | 0.711 | 2 | Fail
12 |  | 12.225 | 4.797 | 0.392 | 2
13 |  | 5.0856 | 1.852 | 0.364 | 2 | Fail
14 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan-Phousacan
15 | PDH.Aerodev |  |  |  |  | Pass |  | B.dan-Phousacan
16 |  | 12.2301 | 4.437 | 0.363 | 2 | Pass
17 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
18 | STM-1 |  |  |  |  | Pass |  | XiengNguen - M.Nan
Update By:
Date:

## Silalek
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Silalek |  |  | TO: |  | XiengNguen
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 24.5878 | 9.375 | 0.381 | 3
2 | Free | 3.355 | 1.923 | 0.573 | 2 | Fail
3 | STM64.Alcatel |  |  |  |  | Pass
4 | STM64.Alcatel |  |  |  |  | Pass
5 | Free | 48.3535 | 20.825 | 0.431 | 7
6 | Free | 24.5776 | 10.121 | 0.412 | 4
7 | PDH.Aerodev |  |  |  |  | Pass |  | XiengNguen-Silalek
8 | Free | 11.7552 | 4.632 | 0.394 | 2
9 | Free | 10.596 | 4.365 | 0.412 | 2
10 | Free | 24.5827 | 9.373 | 0.381 | 4
11 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
12 | Free
13 | Free
14 | PDH.Aerodev |  |  |  |  | Pass |  | XiengNguen-Silalek
15 | STM64.Huawei | [6 empty] | Phonpheng-Xayya
16 | Free
17 | STM64.Huawei | [6 empty] | Phonpheng-Xayya
18 | STM-1 |  |  |  |  | Pass |  | XiengNguen-M.Nan
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Silalek |  |  | TO: |  | B.Dan
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 |  | 10.5705 | 5.692 | 0.538 | 3
2 |  | 8.9977 | 4.414 | 0.491 | 4
3 | STM64.Alcatel |  |  |  |  | Pass
4 | STM64.Alcatel |  |  |  |  | Pass
5 | PDH.Aerodev |  |  |  |  | Pass
6 | STM64.Huawei |  |  |  |  | Pass
7 | STM64.Huawei |  |  |  |  | Pass
8 |  | 10.5705 | 5.324 | 0.504 | 3
9 | STM1.Alcatel |  |  |  |  | Pass
10 |  | 10.5705 | 5.495 | 0.52 | 3
11 | STM1.Alcatel |  |  |  |  | Pass
12 |  | 8.2725 | 4.423 | 0.535 | 1 | Fail
13 | PDH.Aerodev |  |  |  |  | Pass
14 |  | 10.5807 | 5.974 | 0.565 | 3
15 |  | 10.5756 | 7.083 | 0.67 | 4
16 |  | 10.5807 | 5.828 | 0.551 | 3
17 |  | 10.5756 | 8.45 | 0.799 | 3
18 |  | 10.5807 | 6.241 | 0.59 | 3
Update By:
Date:

## Kiewkacham
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Kiewkacham |  |  | TO: |  | Phoukhoun
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | Free | 12.4037 | 4.938 | 0.398 | 9 | Fail
2
3 | Free | 48.0811 | 0.322 | 0.408 | 14 | Pass
4 | Free | 12.4062 | 4.648 | 0.375 | 8 | Fail
5 | Free | 12.4037 | 0.444 | 0.381 | 8 | Fail
6 | DWDM |  |  |  |  | Pass
7 | Free | 31.3054 | 15.48 | 0.494 | 20 | Fail
8 | Free | 5.9823 | 2.398 | 0.401 | 5 | Fail
6 | DWDM |  |  |  |  | Pass
10 | Free | 5.9797 | 2.325 | 0.389 | 6 | Fail
11 | Free | 5.9797 | 2.459 | 0.411 | 7 | Fail
12 | Free | 5.9617 | 2.918 | 0.49 | 6 | Fail
13 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-Phoukhoun
14 | Free | 0.855 | 0.392 | 0.458 | 2 | Fail
2 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-Phoukhoun
16 | Ext.Cell | 7.48 |  |  |  | Pass |  | Cell_NongOn
17 | Ext.Cell | 7.48 |  |  |  | Pass |  | Cell_NongOn
18 | Free | 21.5545 | 8.37 | 0.388 | 17 | Fail
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Kiewkacham |  |  | TO: |  | XiengNguen
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 | Free | 36.3634 | 17.966 | 0.494 | 15
2 | STM64.Alcatel |  |  |  |  | Pass |  | phonepheng-phoukhoun
3 | PDH |  |  |  |  | Pass |  | Kiewkacham-Phonepheng
4 | STM64.Alcatel |  |  |  |  | Pass |  | phonepheng-phoukhoun
5 | Free | 20.5664 | 9.087 | 0.442 | 20 | Fail |  | RPT.Namming
6 | Free | 23.3418 | 11.348 | 0.486 | 21 | Fail |  | RPT.Namming
7 | PTN910 | 45.0049 | 13.69 | 0.428 | 14 | Pass |  | Namkhan3 - Kiewkacham
8 | Free | 17.694 | 8.942 | 0.505 | 17 | Fail
9 | PTN910 | 45.0049 | 13.885 |  |  | Pass |  | Namkhan3 - Kiewkacham
10 | Free | 11.7909 | 5.572 | 0.473 | 13 | Fail
11 | Free | 11.7935 | 5.325 | 0.452 | 16 | Fail
12 | Free | 11.884 | 6.102 | 0.518 | 14 | Fail
13 | Free | 20.1023 |  |  |  | Fail
14 | Free | 20.1023 |  |  |  | Fail
15 | PDH |  |  |  |  | Pass |  | Kiewkacham-Phonepheng
16 | Free | 45.5423 | 17.904 | 0.423 | 22 | Fail
17 | Free | 20.5537 | 8.9903 | 0.433 | 18 | Fail
18 | Free | 20.6405 | 13.664 | 0.662 | 23 | Fail
Update By:
Date:

## Phoukhoun
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phoukhoun |  |  | TO: |  | Kiewkacham
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
|  | 36.7623 | 15.034 | 0.41 | 11
2 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-Phoukhoun
3 |  | 8.7576 | 4.596 | 0.525 | 6
4 |  | 36.6877 | 16.837 | 0.459 | 12
5 |  | 36.6315 | 16.976 | 0.463 | 12
6 |  | 12.8684 | 5.832 | 0.452 | 13
7 |  | 9.7917 | 5.367 | 0.548 | 7
8 |  | 36.2459 | 16.668 | 0.46 | 13
9 |  | 33.0033 | 14.539 | 0.441 | 15
10 | PDH.Aerodev |  |  |  |  | Pass |  | Phoukhoun - Phakengnoy
11 |  | 1.1081 | 1.884 | 1.7 | 1
12 | PDH.Aerodev |  |  |  |  | Pass |  | Phoukhoun - Phakengnoy
13 | STM64.Alcatel |  |  |  |  | Pass |  | Phonepheng-Phoukhoun
14 |  | 34.571 | 15.691 | 0.454 | 8
15 |  | 39.2741 | 15.104 | 0.385 | 9
16 |  | 17.283 | 6.953 | 0.402 | 10
17 |  | 17.7527 | 7.037 | 0.396 | 10
18 |  | 11.9007 | 6.267 | 0.527 | 3
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phoukhoun |  |  | TO: |  | Kasi
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 |  | 37.9004 | 15.081 | 0.398 | 11
2 |  | 4.7669 | 1.802 | 0.378 | 3
3 |  | 37.9056 | 15.022 | 0.396 | 12
4 |  | 17.02 | 6.427 | 0.378 | 9
5 | STM1 | [6 empty] | phoukhoun - Vangvieng
6 | STM64.Alcatel | [6 empty] | phoukhoun - Vangvieng
7 | Ext.Cell.2G | 5.54 |  |  |  | Pass |  | Viengkham
8 |  | 1.463 | 2.487 | 1.7 | 2
9 |  | 29.3726 | 14.464 | 0.492 | 14
10 | STM1 | [6 empty] | phoukhoun - Vangvieng
11 |  | 2.3235 | 6.748 | 2.904 | 2
12 | STM64.Alcatel | [6 empty] | phoukhoun - Vangvieng
13 |  | 10.859 | 4.162 | 0.383 | 7
14 |  | 6.4495 | 2.478 | 0.384 | 3
15 |  | 13.2156 | 6.405 | 0.485 | 9
16 |  | 13.2131 | 5.23 | 0.396 | 9
17 |  | 13.2131 | 5.858 | 0.443 | 6
18 |  | 13.2182 | 5.221 | 0.395 | 2
Update By:
Date:
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phoukhoun |  |  | TO: |  | Xiengkuang
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test result) | Problem Interface (Fault Piont) | Remark
1 | STM16.Alcatel |  |  |  |  | Pass |  | Phoukhoun - Nongtang
2 | DWDM | 12.01 | 3.844 | 0.427 | 15 |  |  | Phoukhoun - Nongtang
3 | PDH.Aerodev |  |  |  |  | Pass |  | Phoukhoun - Phousoung
4 |  | 12.01 | 3.29 | 0.408 | 3
5 | PDH.Aerodev |  |  |  |  | Pass |  | Phoukhoun - Phousoung
6 |  | 12.01 | 3.86 | 3.29
7 | ATN | 12.01 | 3 | 0.381 |  |  |  | Phoukhoun - Phousoung
8 | ATN | 12.01 | 3 | 0.381 |  |  |  | Phoukhoun - Phousoung
9 | DWDM | 36.0391 | 15.587 | 0.432 | 19 |  |  | Phoukhoun - Nongtang
10 | STM16.Alcatel | [6 empty] | Phoukhoun - Nongtang
11 | PDH.Aerodev | [6 empty] | NamNguem 5
12 | PDH.Aerodev | [6 empty] | NamNguem 5
Update By:
Date:

## Phousoung
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phousoung |  |  | TO: | Phouviengnoy
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | PDH | [6 empty] | Phoukhoun - Phousoung
2 | PDH | [6 empty] | Phoukhoun - Phousoung
3 | PDH | [6 empty] | Phousoung - Phouviengnoi
4 | PDH | [6 empty] | Phousoung - Phouviengnoi
5 | ATN910B | 13 |  |  |  |  | NEW | Phoukhoun - Phousoung
6 | ATN910B | 13 |  |  |  |  | NEW | Phoukhoun - Phousoung
7 | ATN910B | 18.5556 |  |  |  |  | NEW | Phousoung - Phouviengnoi
8 | ATN910B | 18.5556 |  |  |  |  | NEW | Phousoung - Phouviengnoi
9
10
11
12
Update By:
Date:
Station From: To: |  | Phousoung |  |  | TO: | Phoukhoun
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1
2
3
4
5
6
7
8
9
10
11
12
Update By:
Date:

## Phouviengnoi
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To: |  | Phouviengnoy |  |  | TO: | Phousoung
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1 | STM64 | [6 empty] | Phoukhoun - Nongtang
2 | STM64 | [6 empty] | Phoukhoun - Nongtang
3 | Free | 22
4 | ATN910B | 18.5556 | [5 empty] | Phouviengnoy - Phousoung
5 | ATN910B | 18.5556 | [5 empty] | Phouviengnoy - Phousoung
6
7 | PDH Aerodev | [6 empty] | Phouviengnoy - Phousoung
8 | PDH Aerodev | [6 empty] | Phouviengnoy - Phousoung
9 | DWDM | [6 empty] | Phoukhoun - Nongtang
10 | DWDM | [6 empty] | Phoukhoun - Nongtang
11 |  | 5.19
12 |  | 5.19
Update By:
Date:
Station From: To: |  | Phouviengnoy |  |  | TO: | Nongtang
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1
2
3
4
5
6
7
8
9
10
11
12
Update By:
Date:

## Form
ຕາຕະລາງເກັບກຳຂໍ້ມູນ Core ສາຍ Optic
Station From: To:
No. Core | Traffic (Equipment) | Distand Core(KM) | Lost (db) | Average Lost db/km | Interface (Closure) QTY | Working (Test resoult) | Problem Interface (Fault Piont) | Remark
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
Update By:
Date: